## LT Batch Calculator
LT POWER CABLE — BATCH SHOULD-COST CALCULATOR
Refresh prices: | https://liveindex.org/mcx-copper/ | https://economictimes.indiatimes.com/commoditysummary/symbol-ALUMINIUM.cms | https://www.plastemart.com/polymer-pricelist/hdpe-reliance-deem-export/2/41 | https://plastemart.com/polymer-pricelist/pvc-reliance/7/9 | https://steel.gov.in/monthly-summery
MATERIAL MASTER | Copper | Aluminium | XLPE | PVC | Steel Wire
Density (g/cm³) | 8.94 | 2.63 | 0.93 | 1.35 | 7.76 |  | Edit density and price directly in these yellow cells; every row on this sheet updates instantly.
Price (Rs/kg) | 1430 | 349 | 135 | 100 | 68
SPECIAL CONSTRUCTION (Y / N)
Configuration label | No. of cores | Shape | Size (sqmm) | Conductor | Insulation | Inner sheath | Armour | Outer sheath | FRLS inner | FRLS outer | LSZH inner | LSZH outer | Oxygen Index | HRPVC inner | HRPVC outer | Extr PVC inner ≤50 | Extr PVC inner 70 | Stranding of cond. | SELLING LOW Rs/m | SELLING HIGH Rs/m | Material cost Rs/m | Approx OD mm | Conductor weight g/m | cond angle | cond dia | cond dens | ins thk | dia/ins | ins dens | neut area | neut dia | neut ins thk | neut core dia | laid-up dia | inner thk | dia/inner | inner dens | armour thk | dia/armour | armour dens | outer thk | dia/outer | outer dens | approx OD | wt cond | wt ins | wt inner | wt outer | wt armour | mat cost | special % | load S1 | load S2 | total S1 | total S2 | selling S1 | selling S2
4C x 25 Cu XLPE | 4 | Circular | 6 | Copper | XLPE | PVC | Galvanised steel round wire | XLPE | N | N | N | N | N | N | N | N | N | N | 410.733 | 434.8938 | 355.442 | 17 | 216.7056 | 360 | 2.764 | 8.94 | 0.7 | 4.164 | 0.93 | 0 | 0 | 0 | 0 | 10.1 | 0.4 | 10.9 | 1.35 | 1.6 | 14.1 | 7.76 | 1.4 | 16.9 | 0.93 | 17 | 216.7056 | 28.621 | 17.991 | 64.0345 | 492.4509 | 355442.0458 | 0% | 0.17647 | 0.11111 | 418167.1127 | 394935.6065 | 434893.7973 | 410733.0307
3.5C x 300 sq.mm CU, XLPE | 3.5 | Circular | 300 | Copper | XLPE | PVC | Unarmored | XLPE | N | N | N | N | N | N | N | N | N | N | 15809.6422 | 16739.6211 | 13681.4211 | 60 | 9480.87 | 360 | 19.5441 | 8.94 | 1.8 | 23.1441 | 0.93 | 150 | 13.8198 | 1.4 | 16.6198 | 52.1 | 0.7 | 53.5 | 1.35 | 0 | 53.5 | 0 | 3.2 | 59.9 | 0.93 | 60 | 9480.87 | 402.9918 | 158.3204 | 535.4109 | 0 | 13681421.1278 | 0% | 0.17647 | 0.11111 | 16095789.5622 | 15201579.0309 | 16739621.1447 | 15809642.1922
3.5C x 240 sq.mm CU, XLPE | 3.5 | Circular | 240 | Copper | XLPE | PVC | Unarmored | XLPE | N | N | N | N | N | N | N | N | N | N | 12654.6461 | 13399.037 | 10951.136 | 55 | 7584.696 | 360 | 17.4808 | 8.94 | 1.7 | 20.8808 | 0.93 | 120 | 12.3608 | 1.2 | 14.7608 | 46.8 | 0.7 | 48.2 | 1.35 | 0 | 48.2 | 0 | 3 | 54.2 | 0.93 | 55 | 7584.696 | 336.6824 | 142.4284 | 453.2579 | 0 | 10951136.0331 | 0% | 0.17647 | 0.11111 | 12883689.4507 | 12167928.9257 | 13399037.0287 | 12654646.0827
3.5C x 185 sq.mm CU, XLPE | 3.5 | Circular | 185 | Copper | XLPE | PVC | Unarmored | XLPE | N | N | N | N | N | N | N | N | N | N | 9798.0234 | 10374.3778 | 8479.0587 | 49 | 5869.11 | 360 | 15.3476 | 8.94 | 1.6 | 18.5476 | 0.93 | 95 | 10.9981 | 1.1 | 13.1981 | 41.6 | 0.6 | 42.8 | 1.35 | 0 | 42.8 | 0 | 2.8 | 48.4 | 0.93 | 49 | 5869.11 | 279.3215 | 108.4598 | 376.7707 | 0 | 8479058.7472 | 0% | 0.17647 | 0.11111 | 9975363.232 | 9421176.3858 | 10374377.7613 | 9798023.4412
3.5C x 150 sq.mm CU, XLPE | 3.5 | Circular | 150 | Copper | XLPE | PVC | Unarmored | XLPE | N | N | N | N | N | N | N | N | N | N | 7841.0426 | 8302.2804 | 6785.5176 | 44 | 4695.288 | 360 | 13.8198 | 8.94 | 1.4 | 16.6198 | 0.93 | 70 | 9.4407 | 1.1 | 11.6407 | 37.2 | 0.6 | 38.4 | 1.35 | 0 | 38.4 | 0 | 2.6 | 43.6 | 0.93 | 44 | 4695.288 | 222.8453 | 97.1512 | 314.5657 | 0 | 6785517.6425 | 0% | 0.17647 | 0.11111 | 7982961.9324 | 7539464.0473 | 8302280.4097 | 7841042.6092
3.5C x 50 sq.mm CU, XLPE | 3.5 | Circular | 50 | Copper | XLPE | PVC | Unarmored | XLPE | N | N | N | N | N | N | N | N | N | N | 2649.9707 | 2805.8514 | 2293.2439 | 28 | 1580.145 | 360 | 7.9788 | 8.94 | 1 | 9.9788 | 0.93 | 25 | 5.6419 | 0.9 | 7.4419 | 22.6 | 0.4 | 23.4 | 1.35 | 0 | 23.4 | 0 | 2.2 | 27.8 | 0.93 | 28 | 1580.145 | 96.861 | 39.4088 | 166.1946 | 0 | 2293243.9181 | 0% | 0.17647 | 0.11111 | 2697934.0213 | 2548048.7979 | 2805851.3821 | 2649970.7498
3C x 50 sq.mm CU, XLPE | 3 | Circular | 2.5 | Copper | XLPE | PVC | Galvanised steel round wire | XLPE | N | N | N | N | N | N | N | N | N | N | 150.4127 | 159.2605 | 130.1648 | 14 | 67.7205 | 360 | 1.7841 | 8.94 | 0.7 | 3.1841 | 0.93 | 0 | 0 | 0 | 0 | 6.9 | 0.4 | 7.7 | 1.35 | 1.6 | 10.9 | 7.76 | 1.4 | 13.7 | 0.93 | 14 | 67.7205 | 15.3938 | 12.508 | 50.8145 | 366.3835 | 130164.8063 | 0% | 0.17647 | 0.11111 | 153135.0663 | 144627.5626 | 159260.4689 | 150412.6651
Note on K8: FRLS PVC inner sheath construction cost Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on L8: FRLS PVC outer sheath construction cost Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on M8: LSZH Inner sheath construction cost Loading: 10.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on N8: LSZH outersheath construction cost Loading: 10.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on O8: Oxygen Index (Outer sheath) Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on P8: HRPVC Inner Sheath Loading: 2.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on Q8: HRPVC Outer Sheath Loading: 2.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on R8: Extruded PVC Inner sheath - Upto 50 sq.mm Loading: 3.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on S8: Extruded PVC Inner sheath - 70 sq.mm Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.
Note on T8: Stranding of Conductor Loading: 1.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 5.

## HT Batch Calculator
HT POWER CABLE — BATCH SHOULD-COST CALCULATOR
Refresh prices: | https://liveindex.org/mcx-copper/ | https://economictimes.indiatimes.com/commoditysummary/symbol-ALUMINIUM.cms | https://www.plastemart.com/polymer-pricelist/hdpe-reliance-deem-export/2/41 | https://plastemart.com/polymer-pricelist/pvc-reliance/7/9 | https://steel.gov.in/monthly-summery
MATERIAL MASTER | Copper | Aluminium | XLPE | PVC | Steel Wire
Density (g/cm³) | 8.94 | 2.63 | 0.93 | 1.35 | 7.76 |  | Edit density and price directly in these yellow cells; every row on this sheet updates instantly.
Price (Rs/kg) | 1345 | 348 | 118 | 101 | 68
SPECIAL CONSTRUCTION (Y / N)
Configuration label | No. of cores | Shape | Size (sqmm) | Conductor | Voltage | Insulation | Inner sheath | Armour | Outer sheath | FRLS inner | FRLS outer | LSZH inner | LSZH outer | Oxygen Index | Extr PVC inner | Press extr PVC inner | SELLING LOW Rs/km | SELLING HIGH Rs/km | Material cost Rs/km | Approx OD mm | Copper weight kg/km | Metallic screen kg/km | Conductor screen kg/km | Insulation screen kg/km | cond angle | cond angle2 | cond dia | cond dens | main ins thk | dia/ins | ins dens | neut area | neut dia | neut ins thk | neut core dia | laid-up dia | inner thk | dia/inner | inner dens | armour thk | dia/armour | armour dens | outer thk | dia/outer | outer dens | approx OD | cond scr wt | ins scr wt | metallic wt | wt cond | wt ins | wt inner | wt outer | wt armour | mat cost | special % | load S1 | load S2 | total S1 | total S2 | selling S1 | selling S2
3.5C x 300 Al 11kV (parity check) | 3.5 | Circular | 300 | Aluminium | 11kV | XLPE | PVC | Galvanised steel flat strip | PVC | N | N | N | N | N | N | N | 2108267.5793 | 2261782.2088 | 1739832.4683 | 79 | 268.2099 | 268.2099 | 17.9433 | 27.8896 | 360 | 0 | 19.5441 | 2.63 | 5.5 | 30.5441 | 0.93 | 150 | 13.8198 | 3.6 | 21.0198 | 68.2 | 0.7 | 69.6 | 1.35 | 1.4 | 72.4 | 7.86 | 2.84 | 78.08 | 1.35 | 79 | 17.5057 | 27.2094 | 262.9509 | 2789.115 | 1219.3927 | 206.5962 | 154.7582 | 2479.0208 | 1739832.4683 | 0% | 0.25 | 0.17647 | 2174790.5854 | 2046861.7275 | 2261782.2088 | 2108267.5793
3C x 240 Al 11kV armoured | 3 | Circular | 240 | Aluminium | 11kV | XLPE | PVC | Galvanised steel round wire | PVC | N | N | N | N | N | N | N | 1915740.7661 | 2055236.4529 | 1580951.1176 | 75 | 255.0091 | 255.0091 | 16.0776 | 26.024 | 360 | 0 | 17.4808 | 2.63 | 5.5 | 28.4808 | 0.93 | 0 | 0 | 0 | 0 | 61.5 | 0.7 | 62.9 | 1.35 | 3.15 | 69.2 | 7.86 | 2.52 | 74.24 | 1.35 | 75 | 15.6855 | 25.3892 | 250.0089 | 1912.536 | 1118.9297 | 186.5063 | 121.463 | 5188.9223 | 1580951.1176 | 0% | 0.25 | 0.17647 | 1976188.8971 | 1859942.4913 | 2055236.4529 | 1915740.7661
1C x 400 Cu 33kV unarmoured | 1 | Circular | 400 | Copper | 33kV | XLPE | PVC | Unarmored | PVC | N | N | N | N | N | N | N | 5960988.5676 | 6436642.0929 | 5208630.7872 | 45 | 3766.113 | 154.353 | 20.6772 | 36.5913 | 360 | 0 | 22.5676 | 8.94 | 8.8 | 40.1676 | 0.93 | 0 | 0 | 0 | 0 | 40.2 | 0.5 | 41.2 | 1.35 | 0 | 41.2 | 0 | 1.88 | 44.96 | 1.35 | 45 | 20.1728 | 35.6989 | 151.3265 | 3611.76 | 814.5503 | 87.1705 | 3.8535 | 0 | 5208630.7872 | 0% | 0.18824 | 0.11111 | 6189078.9354 | 5787367.5414 | 6436642.0929 | 5960988.5676
3C x 95 Al 22kV armoured | 3 | Circular | 95 | Aluminium | 22kV | XLPE | PVC | Galvanised steel round wire | PVC | N | N | N | N | N | N | N | 1139247.6731 | 1222202.6007 | 940155.8467 | 61 | 208.1875 | 208.1875 | 10.2159 | 21.0664 | 360 | 0 | 10.9981 | 2.63 | 6 | 22.9981 | 0.93 | 0 | 0 | 0 | 0 | 49.7 | 0.6 | 50.9 | 1.35 | 2.5 | 55.9 | 7.86 | 2.36 | 60.62 | 1.35 | 61 | 9.9667 | 20.5526 | 204.1054 | 757.0455 | 902.8728 | 129.2779 | 49.4918 | 3329.4696 | 940155.8467 | 0% | 0.25 | 0.17647 | 1175194.8084 | 1106065.702 | 1222202.6007 | 1139247.6731
3C x 150 Cu 6.6kV armoured | 3 | Circular | 150 | Copper | 6.6kV | XLPE | PVC | Galvanised steel flat strip | PVC | N | N | N | N | N | N | N | 6750354.4254 | 7288994.9281 | 5898367.9445 | 50 | 4234.1528 | 170.9228 | 12.7673 | 17.8309 | 360 | 0 | 13.8198 | 8.94 | 2.8 | 19.4198 | 0.93 | 0 | 0 | 0 | 0 | 41.9 | 0.5 | 42.9 | 1.35 | 1.4 | 45.7 | 7.86 | 2.04 | 49.78 | 1.35 | 50 | 12.4559 | 17.396 | 167.5713 | 4063.23 | 411.9632 | 90.8115 | 23.5078 | 1546.7693 | 5898367.9445 | 0% | 0.18824 | 0.11111 | 7008648.9693 | 6553742.1605 | 7288994.9281 | 6750354.4254
Note on L8: FRLS PVC inner sheath construction cost Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.
Note on M8: FRLS PVC outer sheath construction cost Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.
Note on N8: LSZH Inner sheath construction cost Loading: 10.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.
Note on O8: LSZH outersheath construction cost Loading: 10.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.
Note on P8: Oxygen Index (Outer sheath) Loading: 2.5% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.
Note on Q8: Extruded PVC Inner sheath Loading: 3.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.
Note on R8: Pressure Extruded PVC Innersheath Loading: 5.0% of total cost when set to Y. Rate editable on Assumptions & Ref, section 6.

## Assumptions & Ref
POWER CABLE — ASSUMPTIONS & REFERENCE TABLES
1. MATERIAL MASTER (reference copy only — live values are edited on each calculator tab)
Material | Density | Price |  | Status
| g/cm³ | Rs/kg
Copper |  |  |  | Not used in calculations
Aluminium |  |  |  | Not used in calculations
XLPE |  |  |  | Not used in calculations
PVC |  |  |  | Not used in calculations
Steel Wire |  |  |  | Not used in calculations
3. LT COST STRUCTURE (% of total cost — varies by conductor, per the source model)
Cost element | SCENARIO 1 |  | SCENARIO 2 |  |  | Note
| Copper | Aluminium | Copper | Aluminium
Material cost | 85% | 80% | 90% | 85%
Conversion & other | 9% | 13% | 5% | 10%
Transportation | 1% | 1% | 1% | 1%
Drum cost | 1% | 2% | 1% | 1%
Overheads / insurance / finance | 4% | 4% | 3% | 3%
Margin | 4% | 4% | 4% | 4% |  | Applied to cable cost to give selling price
Wastage (all materials) | 1%
4. HT COST STRUCTURE (% of total cost — varies by conductor, per the source model)
Cost element | SCENARIO 1 |  | SCENARIO 2 |  |  | Note
| Copper | Aluminium | Copper | Aluminium
Material cost | 85% | 80% | 90% | 85%
Conversion & other | 9% | 13% | 5% | 10%
Transportation | 1% | 1% | 1% | 1%
Drum cost | 2% | 2% | 1% | 1%
Overheads / insurance / finance | 4% | 4% | 3% | 3% |  | THIS is what drives the HT selling price — see note below
Margin (reference only) | 4% | 4% | 4% | 4% |  | Not used in the HT selling-price step — see note below
Wastage: main materials | 1%
Wastage: metallic screen | 2%
Wastage: semicon screens | 2.5%
NOTE: the source HT model's final selling-price step multiplies by (1 + Overheads %), not by the Margin % field. Reproduced here for exact parity.
5. LT SPECIAL CONSTRUCTION COSTS (loading on total cost when selected 'Y' on the LT tab)
Construction option | Loading % | Column
FRLS PVC inner sheath construction cost | 2.5% | K
FRLS PVC outer sheath construction cost | 2.5% | L
LSZH Inner sheath construction cost | 10% | M
LSZH outersheath construction cost | 10% | N
Oxygen Index (Outer sheath) | 2.5% | O
HRPVC Inner Sheath | 2% | P
HRPVC Outer Sheath | 2% | Q
Extruded PVC Inner sheath - Upto 50 sq.mm | 3% | R
Extruded PVC Inner sheath - 70 sq.mm | 2.5% | S
Stranding of Conductor | 1.5% | T
6. HT SPECIAL CONSTRUCTION COSTS (loading on total cost when selected 'Y' on the HT tab)
Construction option | Loading % | Column
FRLS PVC inner sheath construction cost | 2.5% | L
FRLS PVC outer sheath construction cost | 2.5% | M
LSZH Inner sheath construction cost | 10% | N
LSZH outersheath construction cost | 10% | O
Oxygen Index (Outer sheath) | 2.5% | P
Extruded PVC Inner sheath | 3% | Q
Pressure Extruded PVC Innersheath | 5% | R
7. HT SCREENS & TAPE
Semiconducting compound density (g/cm³) | 0.936
Conductor screen thickness (mm) | 0.3
Insulation screen thickness (mm) | 0.3
Metallic screen tape thickness (mm) | 0.06
Metallic screen: no. of tapes | 2
Metallic screen price = copper × | 1.15
8. LT IS LOOKUP TABLES (do not delete rows; extend at the bottom keeping ascending order)
Insul: area mm² | 1-core armd | multi/unarmd |  | Inner: dia LB | thk |  | Outer: dia LB | nom (unarmd) | min (armd)
1.5 | 1 | 0.7 |  | 0 | 0.3 |  | 0 | 1.8 | 1.24
2.5 | 1 | 0.7 |  | 25 | 0.4 |  | 15 | 2 | 1.4
4 | 1 | 0.7 |  | 35 | 0.5 |  | 25 | 2.2 | 1.56
6 | 1 | 0.7 |  | 45 | 0.6 |  | 35 | 2.4 | 1.72
10 | 1 | 0.7 |  | 55 | 0.7 |  | 40 | 2.6 | 1.88
16 | 1 | 0.7 |  |  |  |  | 45 | 2.8 | 2.04
25 | 1.2 | 0.9 |  |  |  |  | 50 | 3 | 2.2
35 | 1.2 | 0.9 |  |  |  |  | 55 | 3.2 | 2.36
50 | 1.3 | 1 |  |  |  |  | 60 | 3.4 | 2.52
70 | 1.4 | 1.1 |  |  |  |  | 65 | 3.6 | 2.68
95 | 1.4 | 1.1 |  |  |  |  | 70 | 3.8 | 2.84
120 | 1.5 | 1.2 |  |  |  |  | 75 | 4 | 3
150 | 1.7 | 1.4
185 | 1.9 | 1.6
240 | 2 | 1.7
300 | 2.1 | 1.8
400 | 2.4 | 2
500 | 2.6 | 2.2
630 | 2.8 | 2.4
800 | 3.1 | 2.6
1000 | 3.3 | 2.8
Armour: dia LB | strip thk | round dia |  | Neutral: phase mm² | neutral mm²
0 | 0.8 | 1.4 |  | 25 | 16
13 | 0.8 | 1.6 |  | 35 | 16
25 | 0.8 | 2 |  | 50 | 25
40 | 1.4 | 2.5 |  | 70 | 35
55 | 1.4 | 3.15 |  | 95 | 50
70 | 1.4 | 4 |  | 120 | 70
|  |  |  | 150 | 70
|  |  |  | 185 | 95
|  |  |  | 240 | 120
|  |  |  | 300 | 150
|  |  |  | 400 | 185
|  |  |  | 500 | 240
|  |  |  | 630 | 300
9. HT INSULATION THICKNESS (mm, by voltage & area — IS 7098)
Area mm² | 3.3kV | 6.6kV | 11kV earthed | 11kV unearthed | 22kV | 33kV
25 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
35 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
50 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
70 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
95 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
120 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
150 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
185 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
300 | 2.5 | 2.8 | 3.6 | 5.5 | 6 | 8.8
400 | 2.6 | 3.3 | 3.6 | 5.5 | 6 | 8.8
500 | 2.8 | 3.5 | 3.6 | 5.5 | 6 | 8.8
630 | 3 | 3.5 | 3.6 | 5.5 | 6 | 8.8
800 | 3.3 | 3.5 | 3.6 | 5.5 | 6 | 8.8
1000 | 3.5 | 3.6 | 3.6 | 5.5 | 6 | 8.8
10. HT SHEATH / ARMOUR / OUTER TABLES (match: largest lower-bound ≤ value)
Inner: dia LB | thk |  | Armour: dia LB | strip | round |  | Outer: dia LB | thk
0 | 0.3 |  | 0 | 0.8 | 1.4 |  | 0 | 1.24
25 | 0.4 |  | 13 | 0.8 | 1.6 |  | 15 | 1.4
35 | 0.5 |  | 25 | 0.8 | 2 |  | 25 | 1.56
45 | 0.6 |  | 40 | 1.4 | 2.5 |  | 35 | 1.72
55 | 0.7 |  | 55 | 1.4 | 3.15 |  | 40 | 1.88
|  |  | 70 | 1.4 | 4 |  | 45 | 2.04
[7 empty] | 50 | 2.2
[7 empty] | 55 | 2.36
[7 empty] | 60 | 2.52
[7 empty] | 70 | 2.84
[7 empty] | 75 | 3

## Read Me (hidden)
POWER CABLE — BATCH SHOULD-COST CALCULATOR (LT + HT)
Two row-per-configuration calculators. Each carries its own material master (density and price) edited on the sheet itself; cost structures, special-construction loadings and IS tables are shared from Assumptions & Ref.
THE TABS
• LT Batch Calculator — low-tension (1.1 kV) power cables.
• HT Batch Calculator — high-tension (3.3 / 6.6 / 11 / 22 / 33 kV) cables, with conductor, insulation and metallic screens.
• Assumptions & Ref — cost structures (both scenarios, both conductors), special-construction loadings, screen parameters and all IS lookup tables. Its material master is a reference copy only and no longer drives any calculation.
• Read Me — this sheet.
HOW TO USE
1. Fill one row per cable in the yellow input columns. LT: cores, shape, size, conductor, insulation, inner sheath, armour, outer sheath. HT adds a Voltage column, which sets the insulation thickness.
2. Set any special-construction options to 'Y' in the special-construction columns. Hover any of those headers to see its full name and loading %.
3. Read the results in the green columns — the selling price range, material cost, OD, conductor/copper weight (and screen weights on HT).
4. Grey calculation columns hold the full build-up; collapse them with the [-] outline button above them.
5. Density and price are edited in the yellow MATERIAL MASTER block at the top of each calculator (rows 4-6). Cost-structure percentages, special-construction loadings and the IS tables are edited on Assumptions & Ref.
MATERIAL MASTER AND PRICE REFRESH LINKS
Row 3 of each calculator carries a clickable link above each material's column — MCX copper, Economic Times aluminium, Plastemart polymer price lists for XLPE and PVC, and the Ministry of Steel monthly summary. Click through, read the current rate, then type it straight into the yellow Price row beneath. Each calculator holds its own independent copy, so LT and HT can be run on different price dates if you need to; remember to update both when you want them aligned.
SPECIAL CONSTRUCTION COSTS
Each option is a Y/N switch on the calculator; when set to 'Y' its loading is added as a percentage of total cost, exactly as in the source models. Loadings are summed, so multiple options stack.
LT (10 options): FRLS PVC inner sheath 2.5%, FRLS PVC outer sheath 2.5%, LSZH inner sheath 10%, LSZH outer sheath 10%, Oxygen Index (outer sheath) 2.5%, HRPVC inner sheath 2%, HRPVC outer sheath 2%, Extruded PVC inner sheath up to 50 sq.mm 3%, Extruded PVC inner sheath 70 sq.mm 2.5%, Stranding of conductor 1.5%.
HT (7 options): FRLS PVC inner sheath 2.5%, FRLS PVC outer sheath 2.5%, LSZH inner sheath 10%, LSZH outer sheath 10%, Oxygen Index (outer sheath) 2.5%, Extruded PVC inner sheath 3%, Pressure extruded PVC inner sheath 5%.
All rates are editable in sections 5 and 6 of Assumptions & Ref.
WEIGHT OUTPUTS
• LT reports Conductor weight (kg/km) — the conductor metal, whichever it is. HT reports Copper weight (kg/km) — conductor copper where the conductor is Copper, plus the copper metallic screen, which is present on every HT cable regardless of conductor material. Both include wastage, consistent with the costed weights.
• HT also reports Metallic screen, Conductor screen and Insulation screen weights (kg/km), all including their respective wastage allowances (2% metallic, 2.5% semiconducting), matching the 'Including Wastage' column of the source model.
CORRECTION MADE IN THIS VERSION — COST STRUCTURE NOW VARIES BY CONDUCTOR
Both source models set the cost-structure percentages conditionally on conductor material, e.g. Material cost = IF(conductor = Aluminium, 80%, 85%), and similarly for Conversion and Drum. Earlier versions of this workbook applied a single fixed set, which was right for the parity row but wrong for rows using the other conductor. Sections 3 and 4 of Assumptions & Ref now hold a full Copper / Aluminium × Scenario 1 / Scenario 2 grid, and each row picks the right column from its own Conductor input. Aluminium LT rows and Copper HT rows will therefore differ from the earlier version — the current figures are the correct ones.
SCENARIO 1 vs SCENARIO 2
Both scenarios share the same material weights, prices and special-construction loadings; they differ only in the cost-structure split. Scenario 1 is the higher-cost view and Scenario 2 the leaner one, so the two together bound a negotiation range. The Low and High columns take the min and max automatically, so the range stays correct even if you re-tune the percentages.
PARITY WITH THE ORIGINAL MODELS
LT row 9 (3-core 25 sq.mm copper): Scenario 1 Rs 636,776/km, Scenario 2 Rs 601,399/km, material Rs 520,442/km, copper 677.2 kg/km.
HT row 9 (3.5-core 300 sq.mm aluminium, 11 kV, flat-strip armoured): Scenario 1 Rs 1,459,125/km, Scenario 2 Rs 1,360,090/km, material Rs 1,122,404/km; metallic screen 268.2, conductor screen 17.9, insulation screen 27.9 kg/km.
All match the source workbooks exactly. Keep both rows as checks whenever you change an assumption.
QUIRKS CARRIED OVER FROM THE SOURCE MODELS (flagged, not silently changed)
• HT selling price: the source multiplies total cable cost by (1 + Overheads %), not by the separate Margin % field. In Scenario 1 the two coincide at 4%; in Scenario 2 the Overheads rate of 3% applies rather than the stated 4% Margin. Reproduced for exact parity — the HT Margin row on Assumptions & Ref is kept for reference only and does not drive the price.
• HT outer-sheath weight is computed between the rounded-up overall diameter and the diameter under the outer sheath, rather than between the outer-sheath and armour diameters as on LT. Unusual, but required to match the source.
• Sheaths (inner + outer) are priced at the PVC rate regardless of the material named for them; only the insulation takes the XLPE / PVC split.
• One deliberate departure: in the source files the Scenario 2 special-construction adders were linked to Scenario 1's total cost (a copy-paste artefact). Here each scenario's adder is computed on its own total, which is what the '% of total cost' definition intends. With all options set to 'N' — the default — results are identical either way.
Yellow = your input (including the material master). Green = result. Grey = intermediate working.