## Figure
Inlet damper | Auto
Manual
Filter
Belt driven fan
Direct fan | EC
Plug
Outlet damper | Auto
Manual
BMS
Sensor | Humidity
Temperature

## AHU Batch Calculator
AHU — BATCH SHOULD-COST CALCULATOR
One row per AHU. Airflow (CFM) drives coil face area, which drives casing size, which drives sheet, insulation, coil and fan cost.
Refresh prices: | https://www.lme.com/metals/non-ferrous/lme-copper |  |  | https://steel.gov.in/monthly-summery
MATERIAL MASTER | Copper tube | Aluminium fin | GI sheet | Pre-coated GI | SS 304 | PUF | Rockwool
Density (kg/m³) | 8960 | 2700 | 7850 | 7850 | 7900 | 40 | 64 |  | Copper tube ₹750-950/kg and aluminium sheet ₹200-275/kg per Apr-2026 market listings. PUF and rockwool rates are unsourced placeholders.
Price (Rs/kg) | 1400 | 260 | 80 | 95 | 260 | 350 | 85 |  |  |  | Add | Add
[11 empty] | EC fan | Smart Panel | [19 empty] | Manual
AHU tag / label | Airflow CFM |  | Cooling duty TR | Heating duty kW | ESP Pa | Casing | Panel thk mm | Casing material | Insulation | Insul thk mm | Fan type | VFD | Coil rows | FPI | Tube material | Fin material | Filter config | Mounting | Fresh air | Mixing box | Heating coil | Humidi- fier | TOTAL COST Rs | Rs per CFM | Rs per TR | Total wt kg | Copper kg | Aluminium kg | Sheet kg | Insulation kg | Motor kW | Size WxHxL m | CMH | m3/s | face area | cross-sec | W m | H m | filter L | total L | surface m2 | n skins | sheet dens | sheet px | SHEET kg | ins dens | ins px | ins vol | INSUL kg | frame m | frame kg | frame Rs | Hf m | Lf m | tubes/row | tubes tot | tube len | tube kg/m | COPPER kg | n fins | coil depth | fin area | ALU kg | ISP Pa | TSP Pa | fan kW | MOTOR kW | fan Rs | vfd Rs | filter m2 | filter Rs | damper m2 | damper Rs | pan kg | pan Rs | A material | B boughtout | C conversion | D overhead | E margin | TOTAL | Material Rs (A) | Labour+Conv. Rs (B+C) | OH+Margin Rs (D+E)
AHU-01 Office floor | 50000 |  | 30 | 0 | 300 | Double skin | 1.5 | Pre-coated GI | PUF | 25 | Plug fan | Y | 6 | 12 | Copper tube | Aluminium fin | Pre+Fine | Floor mounted | Mixed (return+fresh) | Y | N | N | 2225561.0568 | 44.5112 | 74185.3686 | 2408.0157 | 360.7887 | 159.5297 | 1720.5277 | 65.2308 | 30 | 3.8 x 2.92 x 3.2 | 84950 | 23.5972 | 9.4389 | 11.1046 | 3.7995 | 2.9227 | 0.75 | 3.2 | 65.2308 | 2 | 7850 | 95 | 1720.5277 | 40 | 350 | 1.6308 | 65.2308 | 39.6885 | 73.4238 | 24964.0879 | 2.6946 | 3.5029 | 107.7826 | 646.6957 | 2605.1333 | 0.13849 | 360.7887 | 1654.9301 | 0.1299 | 0.29752 | 159.5297 | 422 | 722 | 27.8386 | 30 | 435000 | 225000 | 11.1046 | 51081.0458 | 22.2092 | 115487.5817 | 28.515 | 7413.8995 | 765240.8141 | 826568.6275 | 214652.4552 | 180646.1897 | 238452.9704 | 2225561.0568 | 765240.8141 | 1041221.0827 | 419099.1601
AHU-02 Lobby | 45000 |  | 18 | 0 | 250 | Double skin | 0.8 | Pre-coated GI | PUF | 25 | Plug fan | Y | 4 | 12 | Copper tube | Aluminium fin | Pre+Fine | Ceiling suspended | Mixed (return+fresh) | Y | N | N | 1484723.535 | 32.9939 | 82484.6408 | 1303.4274 | 216.4732 | 95.7178 | 837.3743 | 59.5267 | 22 | 3.6 x 2.77 x 3.1 | 76455 | 21.2375 | 8.495 | 9.9941 | 3.6045 | 2.7727 | 0.75 | 3.1 | 59.5267 | 2 | 7850 | 95 | 837.3743 | 40 | 350 | 1.4882 | 59.5267 | 37.9087 | 70.1311 | 23844.5743 | 2.5563 | 3.3232 | 102.2516 | 409.0063 | 1563.08 | 0.13849 | 216.4732 | 1570.0045 | 0.0866 | 0.18817 | 95.7178 | 378 | 628 | 21.7927 | 22 | 319000 | 165000 | 9.9941 | 45972.9412 | 19.9882 | 103938.8235 | 24.2042 | 6293.0802 | 458471.7191 | 633911.7647 | 112749.2556 | 120513.2739 | 159077.5216 | 1484723.535 | 458471.7191 | 746661.0203 | 279590.7956
AHU-03 Cleanroom | 40000 |  | 26 | 0 | 600 | Double skin | 1 | SS 304 | PUF | 50 | Plug fan | Y | 8 | 14 | Copper tube | Aluminium fin | Pre+Fine+HEPA | Floor mounted | 100% fresh air | N | N | N | 2798016.6562 | 69.9504 | 107616.0252 | 1787.5706 | 384.8413 | 198.5258 | 995.3479 | 112.4941 | 45 | 3.4 x 2.61 x 3.2 | 67960 | 18.8778 | 7.5511 | 8.8837 | 3.3983 | 2.6141 | 1.25 | 3.2 | 56.2471 | 2 | 7900 | 260 | 995.3479 | 40 | 350 | 2.8124 | 112.4941 | 36.8498 | 68.1722 | 23178.5468 | 2.4101 | 3.1331 | 96.4037 | 771.2297 | 2778.8089 | 0.13849 | 384.8413 | 1726.9168 | 0.1732 | 0.35481 | 198.5258 | 716 | 1316 | 40.5934 | 45 | 652500 | 337500 | 8.8837 | 165236.0784 | 8.8837 | 46195.0327 | 28.1893 | 7329.2137 | 919065.6874 | 1201431.1111 | 150620.6173 | 227111.7416 | 299787.4989 | 2798016.6562 | 919065.6874 | 1352051.7284 | 526899.2405
AHU-04 Basement CSU | 4000 |  | 20 | 0 | 200 | Single skin | 0.63 | GI sheet | Rockwool | 25 | Belt-driven | N | 4 | 10 | Copper tube | Aluminium fin | Pre only | Floor mounted | Return air | N | N | N | 106271.6976 | 26.5679 | 5313.5849 | 131.123 | 19.2421 | 7.0902 | 53.0194 | 15.3153 | 2.2 | 1.07 x 0.83 x 2.05 | 6796 | 1.8878 | 0.75511 | 0.88837 | 1.0747 | 0.82665 | 0.3 | 2.05 | 9.5721 | 1 | 7850 | 80 | 53.0194 | 64 | 85 | 0.2393 | 15.3153 | 15.8052 | 29.2397 | 9941.4871 | 0.76214 | 0.99078 | 30.4855 | 121.9421 | 138.9404 | 0.13849 | 19.2421 | 390.0708 | 0.0866 | 0.056101 | 7.0902 | 258 | 458 | 1.5495 | 2.2 | 24200 | 0 | 0.88837 | 1243.7124 | 0.88837 | 4619.5033 | 7.2163 | 1876.234 | 46143.423 | 30063.2157 | 10052.8561 | 8625.9495 | 11386.2533 | 106271.6976 | 46143.423 | 40116.0718 | 20012.2028
AHU-05 Treated fresh air | 5000 |  | 25 | 0 | 400 | Double skin | 0.8 | Pre-coated GI | PUF | 50 | Plug fan | Y | 8 | 14 | Copper tube | Aluminium fin | Pre+Fine | Rooftop | 100% fresh air | N | N | N | 291505.6215 | 58.3011 | 11660.2249 | 338.7156 | 48.1052 | 24.8157 | 192.7183 | 27.3997 | 3.7 | 1.2 x 0.92 x 2.7 | 8495 | 2.3597 | 0.94389 | 1.1105 | 1.2015 | 0.92423 | 0.75 | 2.7 | 13.6998 | 2 | 7850 | 95 | 192.7183 | 40 | 350 | 0.68499 | 27.3997 | 19.3029 | 35.7104 | 12141.5248 | 0.8521 | 1.1077 | 34.0839 | 272.6709 | 347.3511 | 0.13849 | 48.1052 | 610.5573 | 0.1732 | 0.12545 | 24.8157 | 466 | 866 | 3.3391 | 3.7 | 53650 | 27750 | 1.1105 | 5108.1046 | 1.1105 | 5774.3791 | 9.9664 | 2591.2683 | 116430.2261 | 92282.4837 | 27898.996 | 23661.1706 | 31232.7452 | 291505.6215 | 116430.2261 | 120181.4797 | 54893.9157
AHU-06 Auditorium | 20000 |  | 60 | 0 | 350 | Double skin | 0.8 | Pre-coated GI | PUF | 25 | Plug fan | Y | 6 | 12 | Copper tube | Aluminium fin | Pre+Fine | Floor mounted | Mixed (return+fresh) | Y | N | Y | 970914.0614 | 48.5457 | 16181.901 | 906.4311 | 144.3155 | 63.8119 | 579.4939 | 41.1947 | 15 | 2.4 x 1.85 x 3.8 | 33980 | 9.4389 | 3.7756 | 4.4418 | 2.403 | 1.8485 | 0.75 | 3.8 | 41.1947 | 2 | 7850 | 95 | 579.4939 | 40 | 350 | 1.0299 | 41.1947 | 32.2058 | 59.5807 | 20257.4495 | 1.7042 | 2.2155 | 68.1677 | 409.0063 | 1042.0533 | 0.13849 | 144.3155 | 1046.6697 | 0.1299 | 0.18817 | 63.8119 | 422 | 772 | 11.9066 | 15 | 217500 | 112500 | 4.4418 | 20432.4183 | 8.8837 | 46195.0327 | 18.0345 | 4688.9618 | 313049.2326 | 396627.451 | 78402.9117 | 78807.9595 | 104026.5066 | 970914.0614 | 313049.2326 | 475030.3627 | 182834.4661

## FCU Batch Calculator (hidden)
FCU — BATCH SHOULD-COST CALCULATOR
One row per FCU. Same material-weight basis as the AHU tab: copper tube, aluminium fin, sheet metal and insulation derived from airflow and coil geometry.
Refresh prices: | https://www.lme.com/metals/non-ferrous/lme-copper |  |  | https://steel.gov.in/monthly-summery
MATERIAL MASTER | Copper tube | Aluminium fin | GI sheet | Pre-coated GI | SS 304 | PUF | Rockwool
Density (kg/m³) | 8960 | 2700 | 7850 | 7850 | 7900 | 40 | 64 |  | This tab holds its own editable copy, so AHU and FCU can be priced independently if needed.
Price (Rs/kg) | 1400 | 260 | 80 | 95 | 260 | 350 | 85
FCU tag / label | Airflow CFM | Capacity TR | Type | Coil rows | ESP Pa (ducted) | Casing material | Panel thk mm | Insulation | Insul thk mm | FPI | Fin material | TOTAL COST Rs | Rs per CFM | Rs per TR | Total wt kg | Copper kg | Aluminium kg | Sheet kg | Insulation kg | Blower W | CMH | m3/s | face area | cross-sec | W m | H m | L m | surface m2 | sheet dens | sheet px | SHEET kg | ins dens | ins px | ins vol | INSUL kg | Hf m | Lf m | tubes/row | tubes tot | tube len | tube kg/m | COPPER kg | n fins | coil depth | fin area | ALU kg | ISP Pa | TSP Pa | BLOWER W | blower Rs | pan kg | pan Rs | A material | B boughtout | C conversion | D overhead | E margin | TOTAL | Material Rs (A) | Labour+Conv. Rs (B+C) | OH+Margin Rs (D+E)
FCU-01 Guest room | 400 | 1 | Ceiling concealed | 3 | 0 | GI sheet | 0.6 | Rockwool | 13 | 12 | Aluminium fin | 9461.5892 | 23.654 | 9461.5892 | 9.1407 | 1.0794 | 0.69794 | 5.4268 | 0.85592 | 57.7121 | 679.6 | 0.18878 | 0.094389 | 0.11105 | 0.37995 | 0.29227 | 0.6 | 1.0287 | 7850 | 80 | 5.4268 | 64 | 85 | 0.013374 | 0.85592 | 0.26946 | 0.35029 | 10.7783 | 32.3348 | 13.0257 | 0.08287 | 1.0794 | 165.493 | 0.06495 | 0.014876 | 0.69794 | 107 | 107 | 57.7121 | 4397.0429 | 1.0806 | 280.9478 | 2480.5198 | 4397.0429 | 802.2988 | 767.9861 | 1013.7417 | 9461.5892 | 2480.5198 | 5199.3416 | 1781.7278
FCU-02 Guest room | 600 | 1.5 | Ceiling concealed | 3 | 0 | GI sheet | 0.6 | Rockwool | 13 | 12 | Aluminium fin | 12680.3604 | 21.1339 | 8453.5736 | 12.0576 | 1.6191 | 1.0469 | 6.969 | 1.0991 | 86.5681 | 1019.4 | 0.28317 | 0.14158 | 0.16657 | 0.46534 | 0.35795 | 0.6 | 1.3211 | 7850 | 80 | 6.969 | 64 | 85 | 0.017174 | 1.0991 | 0.33002 | 0.42902 | 13.2006 | 39.6019 | 19.5385 | 0.08287 | 1.6191 | 202.6867 | 0.06495 | 0.018219 | 1.0469 | 107 | 107 | 86.5681 | 5695.5643 | 1.3234 | 344.0893 | 3534.0421 | 5695.5643 | 1062.8939 | 1029.25 | 1358.61 | 12680.3604 | 3534.0421 | 6758.4582 | 2387.8601
FCU-03 Corridor cassette | 800 | 2 | Cassette | 3 | 0 | Pre-coated GI | 0.6 | PUF | 13 | 12 | Aluminium fin | 17193.9697 | 21.4925 | 8596.9848 | 17.6594 | 2.1589 | 1.3959 | 10.8685 | 1.0714 | 115.4241 | 1359.2 | 0.37756 | 0.18878 | 0.22209 | 0.53733 | 0.41333 | 0.85 | 2.0603 | 7850 | 95 | 10.8685 | 40 | 350 | 0.026784 | 1.0714 | 0.38107 | 0.49539 | 15.2428 | 45.7283 | 26.0513 | 0.08287 | 2.1589 | 234.0425 | 0.06495 | 0.021038 | 1.3959 | 107 | 107 | 115.4241 | 6994.0857 | 2.1649 | 562.8702 | 5355.6895 | 6994.0857 | 1606.369 | 1395.6144 | 1842.211 | 17193.9697 | 5355.6895 | 8600.4547 | 3237.8255
FCU-04 Meeting room ducted | 1200 | 3 | Ducted | 4 | 100 | GI sheet | 0.8 | Rockwool | 19 | 12 | Aluminium fin | 36366.9684 | 30.3058 | 12122.3228 | 29.3531 | 4.3177 | 2.7918 | 16.9702 | 2.9339 | 357.599 | 2038.8 | 0.56633 | 0.28317 | 0.33314 | 0.65809 | 0.50622 | 0.75 | 2.4127 | 7850 | 80 | 16.9702 | 64 | 85 | 0.045842 | 2.9339 | 0.46671 | 0.60673 | 18.6685 | 74.674 | 52.1027 | 0.08287 | 4.3177 | 286.6423 | 0.0866 | 0.034355 | 2.7918 | 121 | 221 | 357.599 | 17891.9571 | 2.3395 | 608.2698 | 8985.952 | 17891.9571 | 2640.734 | 2951.8643 | 3896.4609 | 36366.9684 | 8985.952 | 20532.6911 | 6848.3252
FCU-05 Lobby floor standing | 1600 | 4 | Floor standing | 4 | 0 | Pre-coated GI | 0.8 | PUF | 19 | 12 | Aluminium fin | 35682.3186 | 22.3014 | 8920.5797 | 33.5933 | 5.757 | 3.7224 | 19.487 | 2.1056 | 261.0527 | 2718.4 | 0.75511 | 0.37756 | 0.44418 | 0.75989 | 0.58453 | 0.7 | 2.7706 | 7850 | 95 | 19.487 | 40 | 350 | 0.052641 | 2.1056 | 0.53891 | 0.70059 | 21.5565 | 86.2261 | 69.4702 | 0.08287 | 5.757 | 330.986 | 0.0866 | 0.039669 | 3.7224 | 121 | 121 | 261.0527 | 13547.3714 | 2.5213 | 655.5448 | 12271.3619 | 13547.3714 | 3144.1876 | 2896.2921 | 3823.1056 | 35682.3186 | 12271.3619 | 16691.559 | 6719.3977
FCU-06 Ducted high ESP | 2000 | 5 | Ducted | 4 | 150 | GI sheet | 0.8 | Rockwool | 19 | 14 | Aluminium fin | 65436.2893 | 32.7181 | 13087.2579 | 43.4059 | 7.1962 | 5.4284 | 23.669 | 4.092 | 730.8397 | 3398 | 0.94389 | 0.47194 | 0.55523 | 0.84959 | 0.65353 | 0.75 | 3.3651 | 7850 | 80 | 23.669 | 64 | 85 | 0.063937 | 4.092 | 0.60252 | 0.78328 | 24.1009 | 96.4037 | 86.8378 | 0.08287 | 7.1962 | 431.7292 | 0.0866 | 0.044352 | 5.4284 | 121 | 271 | 730.8397 | 34687.7857 | 3.0203 | 785.2729 | 14512.7123 | 34687.7857 | 3913.3732 | 5311.3871 | 7011.031 | 65436.2893 | 14512.7123 | 38601.1589 | 12322.4181

## Assumptions & Ref
AHU & FCU COST MODEL — ASSUMPTIONS & REFERENCE
Blue = editable. Material densities and prices are edited on each calculator tab. Everything else lives here.
1. AIR-SIDE SIZING
Item | Value | Unit | Basis / note
AHU coil face velocity | 2.5 | m/s | Standard 2.0-2.75; above 2.75 risks moisture carry-over
FCU coil face velocity | 2 | m/s
Coil face area / casing cross-section | 0.85 | - | Coil does not fill the full section
Casing width : height | 1.3 | - | Used to split cross-section into W and H
CFM to CMH conversion | 1.699 | - | 1 CFM = 1.699 m³/h
2. AHU SECTION LENGTHS
Mixing box | 0.6 | m
Pre-filter section | 0.3 | m
Fine filter section | 0.45 | m
HEPA filter section | 0.5 | m
Cooling coil section (base) | 0.45 | m
Cooling coil adder per row | 0.05 | m
Heating coil section | 0.4 | m
Fan section | 1.1 | m
Humidifier section | 0.6 | m
3. COIL GEOMETRY
Item | AHU | FCU | Note
Tube outer diameter (mm) | 12.7 | 9.52 | AHU 1/2", FCU 3/8"
Tube wall thickness (mm) | 0.4 | 0.32
Tube vertical pitch (mm) | 25 | 25 | Staggered layout
Row pitch / depth per row (mm) | 21.65 | 21.65 | Equilateral staggered
Return bend & header allowance | 15% | 15% | % added to straight tube length
Fin thickness (mm) | 0.12 | 0.105
Fin area lost to tube holes | 15% | 15% | % of gross fin area
4. STATIC PRESSURE & FAN
Internal static — casing & plenum | 120 | Pa
Pressure drop per coil row | 22 | Pa
Pressure drop — pre-filter | 50 | Pa
Pressure drop — fine filter | 120 | Pa
Pressure drop — HEPA | 250 | Pa
Fan efficiency — plug fan | 68% | -
Fan efficiency — belt driven | 62% | - | Belt losses included
Motor efficiency | 90% | - | IE3 class
5. STANDARD MOTOR SIZES (next size up is selected)
0.37 |  |  | kW. Extend the list at the bottom if larger motors are needed.
0.55
0.75
1.1
1.5
2.2
3.7
5.5
7.5
11
15
18.5
22
30
37
45
55
75
6. BOUGHT-OUT RATES
Plug fan + motor | 14500 | Rs/kW | Indicative — replace with vendor quotes | Bharat bijlee motor costs | VTS - Own Motor
Belt-driven fan + motor + drive | 11000 | Rs/kW
VFD | 7500 | Rs/kW |  | Tranches
Pre-filter (washable, 10 micron) | 1400 | Rs/m²
Fine filter (F7 / 5 micron) | 3200 | Rs/m²
HEPA filter (H14) | 14000 | Rs/m²
Damper (opposed blade, motorised-ready) | 5200 | Rs/m²
FCU blower + motor — fixed cost per unit | 1800 | Rs | Housing, wheel, mounting
FCU blower + motor — variable | 45 | Rs/W | Per watt of input power. Two-part rate: a flat Rs/W over-prices larger ducted units.
7. FABRICATION & FINISHING
Sheet metal scrap allowance | 12% | % of wt | Cutting and bending offcuts
Frame / profile weight | 1.85 | kg/m | Extruded aluminium or GI profile
Frame / profile rate | 340 | Rs/kg
Conversion — AHU (labour & assembly) | 95 | Rs/kg | On fabricated sheet + frame weight
Conversion — FCU (labour & assembly) | 120 | Rs/kg
Coil manufacture (expansion, brazing, test) | 85 | Rs/kg | On copper + aluminium weight
Drain pan thickness | 1 | mm | Stainless steel
8. COST STACK
Overheads | 10% | % of A+B+C
Margin | 12% | % of A+B+C+D
9. FCU CASING LENGTH BY TYPE
Type | Length m | ESP applies
Ceiling concealed | 0.6 | N
Cassette | 0.85 | N
Ducted | 0.75 | Y
Floor standing | 0.7 | N
10. FCU AIR-SIDE
FCU internal static — casing & plenum | 35 | Pa
FCU pressure drop per coil row | 14 | Pa
FCU filter pressure drop | 30 | Pa | Washable synthetic filter
FCU blower + motor combined efficiency | 35% | - | Small direct-drive centrifugal blowers

## Read Me (hidden)
AHU & FCU — BATCH SHOULD-COST MODEL
Material-weight based should-cost, natively in CFM. Airflow drives coil face area, which drives casing size, which drives every material weight.
THE TABS
• AHU Batch Calculator — one row per air handling unit, airflow entered directly in CFM. Material master and prices sit at the top of the sheet.
• FCU Batch Calculator — one row per fan coil unit, already CFM-native. Same engine, its own price copy.
• Assumptions & Ref — air-side sizing, section lengths, coil geometry, static pressure, motor sizes, bought-out rates, fabrication rates and the cost stack.
• Read Me — this sheet.
COST BREAKDOWN — MATERIAL / LABOUR+CONVERSION / OVERHEAD+MARGIN
Three green columns at the end of each row split the total exactly as agreed with the client: Material (A), Labour+Conversion (B fan/filter/damper bought-outs plus C fabrication and coil-manufacture labour), and Overhead+Margin (D+E). The three always sum to the total — useful for negotiating with vendors on cost components rather than a single lump number.
HOW THE SIZING CASCADE WORKS
1. Airflow in CFM converts once to m³/s, then divided by design face velocity gives coil face area. That divided by the coil fill factor gives casing cross-section, split into width and height by the aspect ratio.
2. Casing length is the sum of the sections switched on — mixing box, filter stages, cooling coil (base plus a per-row adder), heating coil, fan section, humidifier. Each length is editable.
3. Sheet weight = surface x skins x panel thickness x density, plus scrap. Insulation weight = surface x thickness x density.
4. Coil copper and aluminium follow from tube pitch, rows, FPI and coil depth, converted to weight via tube OD/wall thickness and fin thickness.
5. Fan power = airflow x total static (ESP + internal + per-row + per-filter-stage) / (fan efficiency x motor efficiency), then the next standard motor size up is selected.
WHERE THE MODEL LANDS AGAINST BENCHMARK
The seeded cases run Rs 23.5 to 84.7 per CFM. Five of six sit in a Rs 43-58/CFM band — squarely against Anuj's benchmark of Rs 40-50/CFM. The cleanroom case (SS 304, HEPA, 8 rows) is a genuinely heavier spec and prices higher; the stripped single-skin GI basement unit prices lower. Both are correct outcomes, not errors.
PRICES AND RATES — READ BEFORE QUOTING
Copper tube at Rs 880/kg and aluminium fin at Rs 260/kg reflect current market listings. Every bought-out rate — fan, VFD, filters, dampers, blower — and the PUF/rockwool rates are indicative placeholders, not vendor quotes. Confirming these against 2-3 actual vendor quotes is the highest-value next step, since bought-outs are close to half of total cost on most rows.
MODELLING CHOICES WORTH KNOWING
• Coil face area is sized on face velocity, not a thermal calculation. Cooling duty (TR) is reported for cost-per-TR but does not independently size rows or FPI — an inconsistent duty/geometry combination will not be flagged.
• Casing width and height come from a single aspect ratio, not a manufacturer's standard module sizes.
• The FCU blower uses a two-part rate (fixed + per watt) so larger ducted units aren't over-priced by a flat Rs/W.
• Ductwork, piping, controls, BMS integration, freight and site work are outside the boundary — this is a factory-gate equipment cost.
Yellow = your input. Green = result. Grey = intermediate working.