## Read Me
Chiller should-cost model
Purpose | Bottom-up should-cost of a chiller from duty to supply price. Built to test against orders and BOQs (first point: D2 TKM, ME.HVAC.HS.1.1, 1,500 TR water-cooled centrifugal, 6.6 kV with VFD). Covers five types: water-cooled centrifugal HT and LT, water-cooled screw, air-cooled screw, air-cooled scroll.
How to use | Add or edit a row on Calculator (yellow cells): type, TR, chilled-water in/out, condenser-water in (or ambient dry-bulb for air-cooled) and range, full-load COP, VFD, ATC, fouling. Enter observed supply and E&C per unit when known; the back-test columns then show the gap. Summary shows the cost stack for any row. Rates sit on the Calculator tab from row 30; the type table sits on Assumptions & Ref.
Method | 1) Duty: evaporator kW = TR x 3.517; shaft kW = duty / COP; heat rejected = duty + shaft. 2) Temperatures: evaporating temp = CHW out minus evap approach; condensing temp from CW out (or ambient) plus approach; Carnot fraction is checked against a ceiling. 3) Heat exchangers: LMTD, fouled U (clean U with fouling resistance), surface area; tubes per pass from flow and velocity; tube length from area; shell diameter from tube count at set pitch; shell thickness from design pressure; steel mass of shell, tubesheets, water boxes and supports. Air-cooled: coil face area from air flow and face velocity. 4) Priced build-up: tubes (mass x rate), fabricated steel, insulation, compressor (power-law on shaft kW), motor, VFD, switchgear, lube, refrigerant, controls, ATC, piping allowance. 5) Stack: assembly and test, logistics, duty, overheads, guarantee provision, OEM margin; E&C as % of supply.
Status of numbers | Every rate and type parameter is an engineering-first placeholder, not a quote or a verified market price. The compressor assembly line is the largest unknown. Calibrate in this order: compressor rate and exponent, tube and shell parameters from an OEM selection, VFD and motor rates, then margin.
Conventions | Blue on yellow = input or typed assumption; black = formula; green font = link from another sheet; green fill = key result. Rupees, ex-GST. Supply scope follows the BOQ header: basic + packing and forwarding + transport + transit insurance + unloading.
Limits | Not modelled: part-load / IPLV performance, water-side pressure drop limits (BOQ: 20 ft evap, 35 ft cond), noise treatment, magnetic-bearing or oil-free premiums, brand and service-network premium beyond the margin line, 3-year AMC (BOQ HS.1.4, quantity on request), chiller plant manager (HS.1.2), pumps, piping.
Checks column | Flags TR above the type's practical max, tube length over the limit, COP above the Carnot-fraction ceiling for the lift, and implausible temperatures. A flag is an input-sanity warning, not an error.

## Calculator
Chiller should-cost: batch calculator
One row per chiller configuration. Edit yellow cells (inputs, and rates in the master block from row 30). Results in groups 8-9. Amounts in Indian rupees, ex-GST, supply scope as BOQ (basic + P&F + freight + insurance).
Colour code: blue on yellow = input or typed assumption; black = formula; green fill = key result. Rows 9-12 are illustrative duties, not orders; overwrite them. Column G is CW inlet for water-cooled and ambient dry-bulb for air-cooled.
1 Configuration (inputs) | [15 empty] | 2 Type lookups |  |  |  | 3 Thermal duty | [8 empty] | 4 Evaporator | [8 empty] | 5 Condenser (water / air) | [11 empty] | 6 Drive |  | 7 Priced build-up, Rs per unit | [17 empty] | 8 Stack and result | [18 empty] | 9 Back-test vs observed
Ref / tag | Chiller type | Capacity per unit | Units | CHW in | CHW out | CW in (WC) / ambient DB (AC) | CW range (WC only) | Full-load COP | VFD | Auto tube cleaning | Evap fouling | Cond fouling | Observed supply per unit | Observed E&C per unit | Source / note | Type row | Water-cooled | HT motor | BPHE evap | Evaporator duty | Compressor shaft power | Heat rejected | Evaporating temp | Condensing temp | Carnot COP | COP as fraction of Carnot | LMTD evaporator | LMTD condenser (WC) | U evap, fouled | Evap surface | CHW flow | Tubes per pass | Total tubes | Tube length | Shell ID | Shell thickness | Steel (shell, tubesheets, boxes, supports) | U cond, fouled | Cond surface | CW flow | Tubes per pass | Total tubes | Tube length | Shell ID | Shell thickness | Steel (shell, tubesheets, boxes, supports) | Air flow (AC) | Coil face area (AC) | Condenser fans (AC) | Motor rated (separate) | Drive / VFD basis | Evap tubes | Evap shell, tubesheets, water boxes | Evap insulation | Evap brazed plate (scroll) | Cond tubes | Cond shell, tubesheets, water boxes | Air-cooled coil, fans, frame | Compressor assembly | Compressor motor | VFD | Switchgear / starter | Lube and oil system | Refrigerant charge | Controls panel | Auto tube cleaning | Refrigerant piping, valves, instruments | Anti-vibration, base, misc | Material subtotal | Assembly and test | Factory performance test | P&F, freight, insurance | Customs duty | Direct cost | Overheads | Guarantee provision | OEM margin | SHOULD-COST SUPPLY per unit | Supply per TR | E&C per unit | Supply + E&C, all units | Group: heat exchangers | Group: compressor and drive | Group: refrigerant, controls, ATC, piping | Group: assembly and test | Group: logistics and duty | Group: overheads, guarantee, margin | Stack check | Observed supply per TR | Model minus observed, per unit | Model vs observed | E&C model vs observed | Checks
|  | TR | nos | deg C | deg C | deg C | K | kW/kW | Yes/No | Yes/No | m2K/kW | m2K/kW | Rs | Rs |  | # | 1/0 | 1/0 | 1/0 | kW | kW | kW | deg C | deg C |  |  | K | K | kW/m2K | m2 | m3/h | nos | nos | m | m | mm | kg | kW/m2K | m2 | m3/h | nos | nos | m | m | mm | kg | m3/s | m2 | nos | kW | kW | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs/TR | Rs | Rs | Rs | Rs | Rs | Rs | Rs | Rs |  | Rs/TR | Rs | % | %
D2 TKM chiller, BOQ ME.HVAC.HS.1.1 | Water-cooled centrifugal, HT 6.6 kV | 1500 | 5 | 17 | 7 | 30 | 5 | 6.5 | Yes | Yes | 0.0176 | 0.044 | 39259510 | 314840 | D2 TKM BOQ (Package 2D, Bidkin). 5 nos; COP min 6.5; CHW 17/7; CW 30/35; 6.6 kV VFD; ATC; 2-yr guarantee. | 1 | 1 | 1 | 0 | 5275.5 | 811.6154 | 6087.1154 | 5.5 | 37 | 8.846 | 73.48% | 4.9095 | 3.9912 | 4.5956 | 233.8236 | 453.698 | 270 | 810 | 4.9 | 1.2091 | 10 | 3688.5936 | 4.0984 | 372.1348 | 1046.9955 | 623 | 1246 | 5 | 1.0868 | 11 | 3320.93 | 0 | 0 | 0 | 930 | 930 | 2480625 | 608617.9444 | 51371.4945 | 0 | 3893750 | 547953.4427 | 0 | 12139183.4057 | 3720000 | 10695000 | 2200000 | 600000 | 495000 | 900000 | 2767400 | 1183290.0772 | 180000 | 42462191.3645 | 5944706.791 | 636932.8705 | 1471314.9308 | 0 | 50515145.9568 | 5051514.5957 | 1010302.9191 | 6789235.6166 | 63366199.0883 | 42244.1327 | 506929.5927 | 319365643.4048 | 7582317.8816 | 29354183.4057 | 5525690.0772 | 6581639.6615 | 1471314.9308 | 12851053.1314 | OK | 26173.0067 | 24106689.0883 | 61.4% | 61.01% | COP high vs lift;
Illustrative: 400 TR LT centrifugal | Water-cooled centrifugal, LT 415 V | 400 | 2 | 12 | 7 | 32 | 5 | 5.8 | Yes | No | 0.0176 | 0.044 |  |  | Illustrative duty. Not an actual order. | 2 | 1 | 0 | 0 | 1406.8 | 242.5517 | 1649.3517 | 5.5 | 39 | 8.3179 | 69.73% | 3.4099 | 3.9912 | 4.5956 | 89.7749 | 241.9723 | 144 | 432 | 3.5 | 0.91942 | 10 | 2094.3863 | 4.0984 | 100.8328 | 283.6916 | 169 | 338 | 5 | 0.61396 | 10 | 1394.0259 | 0 | 0 | 0 | 280 | 280 | 945000 | 345573.7421 | 27902.4147 | 0 | 1056250 | 230014.2744 | 0 | 4619050.9139 | 644000 | 1680000 | 206000 | 400000 | 132000 | 700000 | 0 | 433427.4807 | 180000 | 11599218.8258 | 1623890.6356 | 173988.2824 | 401912.9323 | 0 | 13799010.6761 | 1379901.0676 | 275980.2135 | 1854587.0349 | 17309478.9921 | 43273.6975 | 138475.8319 | 34895909.6481 | 2604740.4312 | 7549050.9139 | 1445427.4807 | 1797878.918 | 401912.9323 | 3510468.316 | OK |  |  |  |  | COP high vs lift;
Illustrative: 250 TR water-cooled screw | Water-cooled screw, LT 415 V | 250 | 2 | 12 | 7 | 32 | 5 | 5 | No | No | 0.0176 | 0.044 |  |  | Illustrative duty. Not an actual order. | 3 | 1 | 0 | 0 | 879.25 | 175.85 | 1055.1 | 5 | 39.5 | 8.0623 | 62.02% | 3.9912 | 4.5512 | 3.5618 | 61.8505 | 151.2327 | 100 | 200 | 5.2 | 0.66873 | 10 | 1604.3379 | 3.7563 | 61.7181 | 181.4792 | 120 | 240 | 4.3 | 0.53309 | 10 | 1050.6956 | 0 | 0 | 0 | 0 | 205 | 650000 | 264715.7515 | 30151.8545 | 0 | 645000 | 173364.7689 | 0 | 2095713.3992 | 0 | 0 | 172250 | 0 | 67500 | 500000 | 0 | 231536.7464 | 180000 | 5010232.5206 | 701432.5529 | 75153.4878 | 173604.5568 | 0 | 5960423.1181 | 596042.3118 | 119208.4624 | 801080.8671 | 7476754.7594 | 29907.019 | 59814.0381 | 15073137.5949 | 1763232.3749 | 2267963.3992 | 979036.7464 | 776586.0407 | 173604.5568 | 1516331.6412 | OK
Illustrative: 150 TR air-cooled screw | Air-cooled screw, LT 415 V | 150 | 2 | 12 | 7 | 43 |  | 3 | No | No | 0.0176 |  |  |  | Illustrative duty. Not an actual order. Col G = ambient DB. | 4 | 0 | 0 | 0 | 527.55 | 175.85 | 703.4 | 4 | 58 | 5.1324 | 58.45% | 5.0977 | 0 | 3.0294 | 34.1612 | 90.7396 | 60 | 120 | 4.8 | 0.54843 | 10 | 1166.7153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.7536 | 22.7015 | 12 | 0 | 205 | 360000 | 192508.0316 | 22825.4153 | 0 | 0 | 0 | 1985764.8912 | 2095713.3992 | 0 | 0 | 172250 | 0 | 36000 | 400000 | 0 | 279408.7042 | 180000 | 5724470.4416 | 801425.8618 | 85867.0566 | 198352.9008 | 0 | 6810116.2608 | 681011.6261 | 136202.3252 | 915279.6255 | 8542609.8376 | 56950.7323 | 68340.8787 | 17221901.4326 | 2561098.3381 | 2267963.3992 | 895408.7042 | 887292.9184 | 198352.9008 | 1732493.5768 | OK
Illustrative: 60 TR air-cooled scroll | Air-cooled scroll, LT 415 V (modular) | 60 | 2 | 12 | 7 | 43 |  | 2.9 | No | No | 0.0176 |  |  |  | Illustrative duty. Not an actual order. Col G = ambient DB. | 5 | 0 | 0 | 1 | 211.02 | 72.7655 | 283.7855 | 4 | 57 | 5.2292 | 55.46% | 5.0977 | 0 | 4.1698 | 9.9274 | 36.2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.8972 | 9.1589 | 5 | 0 | 85 | 0 | 0 | 0 | 109201.6329 | 0 | 0 | 809877.5595 | 694556.2831 | 0 | 0 | 118250 | 0 | 10800 | 250000 | 0 | 96818.1285 | 180000 | 2269503.6041 | 317730.5046 | 34042.5541 | 78638.2999 | 0 | 2699914.9626 | 269991.4963 | 53998.2993 | 362868.571 | 3386773.3291 | 56446.2222 | 27094.1866 | 6827735.0315 | 919079.1925 | 812806.2831 | 537618.1285 | 351773.0586 | 78638.2999 | 686858.3665 | OK
Material master and rates (edit here; blue on yellow). Every named cell is r_...
Item | Value | Unit | Basis / status
Geometry and thermal constants
Specific heat of water | 4.186 | kJ/kgK | Physical constant
Tube outside diameter | 19.05 | mm | 3/4 inch enhanced copper tube, common in chiller bundles
Tube wall thickness | 0.9 | mm | Assumption
Tube flow area (inside) | 0.00023371 | m2 | Formula
Enhanced copper tube mass | 0.5 | kg/m | Assumption incl. integral fins
Tube pitch ratio (pitch / OD) | 1.25 | x | Triangular layout
Bundle fill factor | 0.8 |  | Assumption
Shell clearance added to bundle diameter | 0.1 | m | Assumption
Flooded-evaporator shell oversize (vapour disengagement) | 1.35 | x | Assumption
Maximum tube length before flag | 9 | m | Practicality limit, flag only
Max credible fraction of Carnot COP at full load | 0.68 |  | Flag only; assumption, check with OEM data
Specific heat of air | 1.006 | kJ/kgK | Physical constant
Air density at coil | 1.12 | kg/m3 | At about 40 C
Air temperature rise across condenser coil | 11 | K | Assumption
Coil face velocity | 2.5 | m/s | Assumption
Air per condenser fan | 5 | m3/s | Assumption
Motor efficiency | 0.96 |  | Assumption
Motor sizing margin on shaft power | 1.1 | x | Assumption
Pressure shell and fabrication
Evaporator design pressure | 10 | bar | HFC-134a class, assumption
Condenser design pressure | 15 | bar | HFC-134a class, assumption
Allowable stress x joint efficiency | 117 | MPa | 138 MPa x 0.85, assumption
Corrosion allowance | 3 | mm | Assumption
Minimum shell thickness | 10 | mm | Assumption
Tubesheet thickness | 40 | mm | Assumption
Water boxes and covers as multiple of tubesheet steel | 1.5 | x | Assumption
Supports and saddles as share of steel | 0.1 |  | Assumption
Steel density | 7850 | kg/m3 | Physical constant
Material and bought-out rates (UNVERIFIED placeholders)
Enhanced copper tube, supplied | 1250 | Rs/kg | Placeholder; replace with MCX copper + tube conversion
Fabricated pressure-vessel steel | 165 | Rs/kg | Placeholder; plate + fabrication + testing
Evaporator insulation 25 mm nitrile, laminated | 2400 | Rs/m2 | Placeholder
Brazed plate heat exchanger | 11000 | Rs/m2 | Placeholder
Air-cooled condenser coil (Cu tube, Al fin) | 32000 | Rs/m2 face | Placeholder
Condenser fan with EC motor | 55000 | Rs each | Placeholder
Frame and casing steel for air-cooled unit | 160 | kg/m2 face | Placeholder
Compressor motor 6.6 kV open TEWAC | 4000 | Rs/kW | Placeholder
Compressor motor 415 V | 2300 | Rs/kW | Placeholder
Medium-voltage VFD, 6.6 kV | 11500 | Rs/kW | Placeholder
LV VFD, 415 V | 6000 | Rs/kW | Placeholder
HT switchgear, VCB panel, protection, control transformer | 2200000 | Rs/unit | Placeholder; BOQ calls for VCB with PS-class CTs
LV starter panel, fixed | 80000 | Rs/unit | Placeholder
LV starter panel, per kW | 450 | Rs/kW | Placeholder
Refrigerant HFC-134a, supplied | 600 | Rs/kg | Placeholder
Automatic tube cleaning, per condenser tube | 1900 | Rs/tube | Placeholder
Automatic tube cleaning, fixed (tanks, arrester, PLC panel) | 400000 | Rs/unit | Placeholder
Refrigerant piping, valves, relief, instruments, flow switches | 6% | of HX + compressor | Assumption
Anti-vibration mounts, base frame, misc | 180000 | Rs/unit | Placeholder
Conversion, logistics and commercial stack (UNVERIFIED)
Assembly, piping fabrication, leak and pressure test | 14% | of material | Assumption
Factory performance test (AHRI test bed) | 1.5% | of material | Assumption
Packing, forwarding, freight, insurance to site | 3% | of material + conversion | BOQ rate includes P&F, sea freight, port, transit insurance
Customs duty on imported content | 0% | of material | Set above 0 if the OEM supplies an imported unit
Overheads | 10% | of direct | Assumption
Guarantee provision (24 months, spares, uptime) | 2% | of direct | BOQ requires 2-year guarantee incl. spares
OEM margin | 12% | of direct + OH + guarantee | Assumption
Erection, positioning, commissioning (E&C) | 0.8% | of supply | Single point: D2 TKM BOQ Rs 3.15 lakh on Rs 3.93 crore

## Summary
Chiller should-cost: summary
Configuration row to show (1-20) | 1
Key results
Ref / tag | D2 TKM chiller, BOQ ME.HVAC.HS.1.1
Type | Water-cooled centrifugal, HT 6.6 kV
Capacity per unit (TR) | 1500
Units | 5
Compressor shaft power (kW) | 811.6154
Heat rejected (kW) | 6087.1154
Evaporating / condensing temp (C) | 5.5 / 37.0
COP as fraction of Carnot | 73.48%
Evaporator surface (m2) | 233.8236
Condenser surface (m2), water-cooled | 372.1348
Evap tubes x length (nos x m) | 810 x 4.9 m
Cond tubes x length (nos x m) | 1246 x 5.0 m
Should-cost supply per unit (Rs) | 63366199.0883
Supply per TR (Rs) | 42244.1327
Supply, all units (Rs crore) | 31.6831
Observed supply per unit (Rs) | 39259510
Model vs observed | 61.4%
Checks | COP high vs lift;
Cost stack, per unit
Cost group | Rs | Share
Heat exchangers (tubes, shells, boxes, coil, BPHE) | 7582317.8816 | 11.97%
Compressor and drive (compressor, motor, VFD, switchgear, lube) | 29354183.4057 | 46.32%
Refrigerant, controls, ATC, piping, misc | 5525690.0772 | 8.72%
Assembly and factory test | 6581639.6615 | 10.39%
Logistics and duty | 1471314.9308 | 2.322%
Overheads, guarantee, margin | 12851053.1314 | 20.28%
SHOULD-COST SUPPLY per unit | 63366199.0883 | 100%
Check against Calculator | OK
All configurations
# | Ref / tag | Type | TR | Units | Model supply per unit (Rs) | Model Rs/TR | Observed per unit (Rs) | Observed Rs/TR | Model vs observed | Checks
1 | D2 TKM chiller, BOQ ME.HVAC.HS.1.1 | Water-cooled centrifugal, HT 6.6 kV | 1500 | 5 | 63366199.0883 | 42244.1327 | 39259510 | 26173.0067 | 61.4% | COP high vs lift;
2 | Illustrative: 400 TR LT centrifugal | Water-cooled centrifugal, LT 415 V | 400 | 2 | 17309478.9921 | 43273.6975 |  |  |  | COP high vs lift;
3 | Illustrative: 250 TR water-cooled screw | Water-cooled screw, LT 415 V | 250 | 2 | 7476754.7594 | 29907.019
4 | Illustrative: 150 TR air-cooled screw | Air-cooled screw, LT 415 V | 150 | 2 | 8542609.8376 | 56950.7323
5 | Illustrative: 60 TR air-cooled scroll | Air-cooled scroll, LT 415 V (modular) | 60 | 2 | 3386773.3291 | 56446.2222
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20

## Assumptions & Ref
Assumptions & reference: chiller type table
Every value is an engineering-first assumption (blue on yellow = editable). Replace with OEM selection data as it arrives. Rows 6-10 feed the Calculator by type name.
Chiller type | Code | Water-cooled (1) / air-cooled (0) | Compressor class | Motor voltage class | Max TR per unit (flag only) | Evap approach, CHW out to evap temp (K) | Cond approach (K): WC = cond temp minus CW out; AC = cond temp minus ambient DB | U clean, evaporator (kW/m2K, outside-tube basis) | U clean, water condenser (kW/m2K) | Evap tube passes | Cond tube passes | Tube-side velocity (m/s) | Evap construction | Compressor assembly Rs/kW shaft at reference | Reference shaft kW | Scale exponent | Motor priced separately (1) / inside compressor (0) | Lube / oil system lump (Rs per unit) | Controls panel lump (Rs per unit) | Refrigerant charge (kg per TR)
Water-cooled centrifugal, HT 6.6 kV | WCC-HT | 1 | Centrifugal | HT | 3500 | 1.5 | 2 | 5 | 5 | 3 | 2 | 2 | S&T | 15000 | 800 | 0.8 | 1 | 600000 | 900000 | 0.55
Water-cooled centrifugal, LT 415 V | WCC-LT | 1 | Centrifugal | LT | 800 | 1.5 | 2 | 5 | 5 | 3 | 2 | 2 | S&T | 15000 | 800 | 0.8 | 1 | 400000 | 700000 | 0.55
Water-cooled screw, LT 415 V | WCS | 1 | Screw | LT | 500 | 2 | 2.5 | 3.8 | 4.5 | 2 | 2 | 1.8 | S&T | 11000 | 300 | 0.85 | 0 | 0 | 500000 | 0.45
Air-cooled screw, LT 415 V | ACS | 0 | Screw | LT | 450 | 3 | 15 | 3.2 | 0 | 2 | 0 | 1.8 | S&T | 11000 | 300 | 0.85 | 0 | 0 | 400000 | 0.4
Air-cooled scroll, LT 415 V (modular) | ACSc | 0 | Scroll | LT | 250 | 3 | 14 | 4.5 | 0 | 0 | 0 | 0 | BPHE | 9500 | 80 | 0.95 | 0 | 0 | 250000 | 0.3
How to read the type table
Approaches and U values | Typical-range engineering assumptions for flooded S&T centrifugal, flooded/DX S&T screw, finned-coil air-cooled and brazed-plate scroll evaporators. They are not OEM data. Selection software output (tube count, length, surface area) from any chiller offer should replace them first.
Compressor assembly rate | Centrifugal (impellers, gear, guide vanes, bearings, casing) and screw compressors are OEM-proprietary. They are priced as Rs/kW shaft power at a reference size, scaled by a power law. This is the weakest line in the model; back-test first against it.
Rates | All rates on the Calculator tab (copper, plate, VFD, motor, refrigerant, lumps, mark-ups) are unverified placeholders. A web check for MCX copper and BigMint plate prices returned no usable figures, so none is cited. Update from live sources before relying on absolute numbers.
E&C | Erection and commissioning is a percentage of supply, set from the single D2 TKM BOQ point (Rs 3.15 lakh on Rs 3.93 crore per unit). Treat as one data point.
Out of scope | 3-year AMC, chiller plant manager / optimiser, chilled and condenser water pumps, piping, valves and electrical power cabling are separate BOQ lines and are not in this model.