## Read Me
HT switchgear board: should-cost model
Bottom-up cost of a switchboard from its bay schedule. Not a vendor price list: every rate is an editable assumption.
Purpose | Estimate the ex-works price of a 3.3-33 kV metal-clad VCB board from the schedule of bays. Each bay is costed from its sheet steel, switching device, instrument transformers, protection, wiring and test; the board adds the main busbar, DC system, labour, test, packing, overheads and margin.
How to use | Edit the yellow cells on Inputs (board rating and the bay schedule) and, if you have quotes, on Rates. Everything else is a live formula. Results are on Summary; the per-bay build-up is on Bay Costing.
Sheets | Inputs: board specification and bay schedule. Rates: every price, constant and multiplier (named cells, prefix r_). Bay Costing: cost per bay type and board-level items. Summary: cost stack, per-bay and per-ampere figures. Presets: three sample boards to copy into Inputs.
Conventions | Yellow fill = input. Blue font = a typed assumption you may change. Black = formula. Green fill = key output. All amounts are Indian rupees, ex-GST, ex-works.
Basis of the numbers | Device prices scale with rating from an assumed base price: VCB = base(kV) x (A/1250)^0.45 x (kA/25)^0.5. Panel steel, CT, VT and surge-arrester prices are tabulated by voltage class. Steel, copper and aluminium follow commodity prices you type into Rates.
Reasonableness | About Rs 8-10 lakh per 11 kV panel and Rs 20-25 lakh per 33 kV panel at the default rates. These are market ranges, not quotations. Calibrate Rates with two or three recent offers before relying on a figure.
Limits | Single board per workbook (copy the file for another). Busbar sized by current density only (no short-circuit or temperature-rise check). No GST, freight to site, erection or civil work. Fault levels above 40 kA need manufacturer confirmation.
Companion | The same model runs interactively in the Should-Cost dashboards (switchgear.html), with a 3D view and a month selector for the commodity prices.

## Inputs
HT board: specification and bay schedule
Tag / board name | HT-01 11 kV plant board, 13 panels
System voltage | 11 | kV
Busbar rating | 1250 | A
Fault level (3 s) | 25 | kA
Degree of protection | IP42
Arc-fault protection (IAC) | No
Protection relay | Numeric O/C + E/F |  | pick from list
Bay schedule
Bay type | Quantity | Size | Unit
Incomer VCB panel | 2 | 1250 | A
Outgoing feeder VCB panel | 6 | 630 | A
Bus coupler VCB panel | 1 | 1250 | A
Motor feeder VCB panel | 2 | 400 | A
Bus PT, metering and surge-arrester panel | 2
Size: rated current (A) for breakers and feeders, motor kW for starters, kVAr for APFC banks. Quantity 0 removes a bay type.

## Summary
HT board: should-cost summary
HT-01 11 kV plant board, 13 panels
Cost group | Rs | Share | Note
Enclosure & structure | 886939.2 | 7.99% | Sheet steel, pre-treatment, powder coat, doors
Busbars & insulation | 841691.9062 | 7.583% | Main (and vertical) busbar, sleeving
Switching devices | 3818683.4268 | 34.4% | VCBs
Protection & metering | 1482500 | 13.36% | CTs, VTs, relays, meters, arresters
Wiring & auxiliaries | 1013700 | 9.132% | Control wiring, interlocks, DC system, arc detection
Assembly, test, packing & transport | 1214375.4077 | 10.94% | Labour, routine and type tests, packing
Direct cost | 9257889.9408 | 83.4%
Overheads | 833210.0947 | 7.506%
Margin | 1009110.0035 | 9.091%
SHOULD-COST, ex-works (Rs) | 11100210.039 | 100%
Should-cost (Rs crore) | 1.11
Number of bays (units) | 13
Cost per bay (Rs) | 853862.3107
Cost per ampere of busbar (Rs/A) | 8880.168
Sheet steel (kg) | 8820
Busbar mass (kg) | 542.3438
Checks
Largest bay rating within the busbar rating? | OK
Fault level within the usual range? | OK

## Bay Costing
Cost per bay and board-level items
Rows follow the bay schedule on Inputs. Rs per bay unless stated.
Enclosure multiplier (IP x form x arc) |  |  |  | 1
Bay type | Qty | Size A | Steel kg / bay | Sheet steel | Powder coat | Gaskets, doors | VCB | CT set | Relay and meter | VT / arrester | Aux + wiring | Total per bay | Total (qty x)
Incomer VCB panel | 2 | 1250 | 700 | 53200 | 9800 | 7392 | 450000 | 34000 | 69500 | 62400 | 48400 | 734692 | 1469384
Outgoing feeder VCB panel | 6 | 630 | 700 | 53200 | 9800 | 7392 | 330602.5927 | 34000 | 60000 | 0 | 48400 | 543394.5927 | 3260367.5564
Bus coupler VCB panel | 1 | 1250 | 700 | 53200 | 9800 | 7392 | 450000 | 34000 | 69500 | 0 | 48400 | 672292 | 672292
Motor feeder VCB panel | 2 | 400 | 700 | 53200 | 9800 | 7392 | 242533.9352 | 34000 | 60000 | 0 | 48400 | 455325.9352 | 910651.8705
Bus PT, metering and surge-arrester panel | 2 | 0 | 560 | 42560 | 7840 | 5913.6 | 0 | 0 | 48600 | 99000 | 10400 | 214313.6 | 428627.2
Board-level items
Item | Qty | Unit |  | Rate Rs |  |  |  | Amount Rs | Group
Main busbar (copper) | 542.3438 | kg |  | 1495 |  |  |  | 810803.9062 | Busbars & insulation
Busbar sleeving, supports and barriers | 78 | m |  | 396 |  |  |  | 30888 | Busbars & insulation
110 V DC system | 1 | set |  | 402000 |  |  |  | 402000 | Wiring & auxiliaries
Arc-flash detection and fast tripping | 0 | set |  | 202000 |  |  |  | 0 | Wiring & auxiliaries
Earth bar, nameplates, end covers | 13 | column |  | 4500 |  |  |  | 58500 | Wiring & auxiliaries
Assembly, fabrication and wiring labour | 8820 | kg |  | 57 |  |  |  | 502740 | Assembly & test
Routine tests, FAT and inspection | 13 | bay |  | 11700 |  |  |  | 152100 | Assembly & test
Type-test and certification allowance | 1 | lot |  | 160870.2907 |  |  |  | 160870.2907 | Assembly & test
Packing and transport | 1 | lot |  | 398665.1171 |  |  |  | 398665.1171 | Assembly & test
Helper figures
Number of bays (units) | 13
Columns / panels | 13
Board length m (columns x width) | 10.4
Busbar run length m (board + 1.2 m risers per column) | 26
Busbar section mm2 per phase | 781.25
Sheet steel total kg | 8820

## Rates
Rates and constants
Blue = assumption. Replace with quotes. Each value is a named cell (r_...), so formulas stay readable.
Commodity rates
Copper (busbar) | 1400 | Rs/kg | Commodity file / LME x USDINR
CRCA sheet | 76 | Rs/kg
Voltage-class tables
kV | VCB base Rs (1250 A, 25 kA) | Panel steel kg | CT set Rs | VT set Rs | Surge arrester Rs
3.3 | 380000 | 620 | 26000 | 60000 | 14000
6.6 | 390000 | 640 | 28000 | 66000 | 16000
11 | 450000 | 700 | 34000 | 78000 | 21000
22 | 720000 | 1050 | 62000 | 140000 | 48000
33 | 950000 | 1450 | 88000 | 210000 | 70000
Switching devices and protection
VCB rating exponent (A/1250) | 0.45
VCB fault-level exponent (kA/25) | 0.5
Motor-feeder VCB factor | 0.9 | x
CT price growth per unit of (kA/25 - 1) | 0.15
Multi-function meter | 22000 | Rs
Earth switch, interlocks, trip-circuit supervision, heaters, lamps | 38000 | Rs/bay
Factor for 22 kV and above | 1.6 | x
Incomer / coupler relay factor | 1.25 | x
PT-panel relay factor | 0.7 | x
Incomer VT factor (of VT set) | 0.8 | x
Protection relay prices
Electromechanical | 14000 | Rs
Numeric O/C + E/F | 38000 | Rs
IED, IEC 61850 + disturbance record | 98000 | Rs
Busbar and DC system
Busbar current density (copper) | 1.6 | A/mm2
Panel width | 0.8 | m
Busbar fabrication, plating | 95 | Rs/kg
Sleeving, supports, barriers | 220 | Rs/m per phase
HT sleeving factor | 1.8 | x
110 V DC system (battery, charger), base | 220000 | Rs
DC distribution per bay | 14000 | Rs/bay
Arc-flash detection, base | 85000 | Rs
Arc-flash detection per bay | 9000 | Rs/bay
HT wiring factor | 1.6 | x
Control wiring and terminals | 6500 | Rs/bay
HT assembly labour factor | 1.5 | x
HT routine-test factor | 1.8 | x
Enclosure multipliers
IP42 | 1
IP54 | 1.1
IP55 | 1.14
Arc-proof (internal arc classified) enclosure | 1.2 | x
Shop floor, test and cost stack
Pre-treatment and powder coating | 14 | Rs/kg steel
Gaskets, doors, hardware | 6 | Rs/kg steel
Hardware as share of sheet price | 0.06 | x
Assembly, fabrication and wiring labour | 38 | Rs/kg steel
Routine tests, FAT and inspection | 6500 | Rs/bay
Type-test and certification allowance | 2% | of material
Earth bar, nameplates, end covers | 4500 | Rs/column
Packing | 2.5% | of ex-works
Transport to site | 2% | of ex-works
Overheads | 9% | of direct
Margin | 10% | of direct + overheads

## Presets
Sample boards (copy the values into Inputs)
Board | kV | Busbar A | kA
HT-01 11 kV plant board, 13 panels | 11 | 1250 | 25 | inc=2@1250; fdr=6@630; cpl=1@1250; mtr=2@400; pt=2 | IP42, arc No, Numeric O/C + E/F
HT-02 33 kV main board, 8 panels | 33 | 2000 | 31.5 | inc=2@2000; fdr=4@1250; cpl=1@2000; mtr=0; pt=1 | IP42, arc Yes, IED, IEC 61850 + disturbance record
HT-03 6.6 kV motor board, 10 panels | 6.6 | 1250 | 40 | inc=1@1250; fdr=1@630; cpl=0; mtr=7@400; pt=1 | IP42, arc No, Numeric O/C + E/F