## Read Me
LT switchgear board: should-cost model
Bottom-up cost of a switchboard from its bay schedule. Not a vendor price list: every rate is an editable assumption.
Purpose | Estimate the ex-works price of a 415 V LT board (PCC / MCC / APFC) from the schedule of bays. Each bay is costed from its sheet steel, switching device, instrument transformers, protection, wiring and test; the board adds the main busbar, labour, test, packing, overheads and margin.
How to use | Edit the yellow cells on Inputs (board rating and the bay schedule) and, if you have quotes, on Rates. Everything else is a live formula. Results are on Summary; the per-bay build-up is on Bay Costing.
Sheets | Inputs: board specification and bay schedule. Rates: every price, constant and multiplier (named cells, prefix r_). Bay Costing: cost per bay type and board-level items. Summary: cost stack, per-bay and per-ampere figures. Presets: three sample boards to copy into Inputs.
Conventions | Yellow fill = input. Blue font = a typed assumption you may change. Black = formula. Green fill = key output. All amounts are Indian rupees, ex-GST, ex-works.
Basis of the numbers | Device prices scale with rating from an assumed base price: ACB = 2.1 lakh x (A/1000)^0.9 x (kA/50)^0.3 (x1.25 for 4-pole); MCCB = 80 x A^1.05 x (kA/36)^0.35; starters, VFDs and APFC banks scale with kW / kVAr. Steel, copper and aluminium follow commodity prices you type into Rates.
Reasonableness | About Rs 1-4 lakh per LT bay at the default rates (an MCC starter module Rs 0.5-1.5 lakh, an ACB bay Rs 5-12 lakh). These are market ranges, not quotations. Calibrate Rates with two or three recent offers before relying on a figure.
Limits | Single board per workbook (copy the file for another). Busbar sized by current density only (no short-circuit or temperature-rise check). No GST, freight to site, erection or civil work. Fault levels above 65 kA need manufacturer confirmation.
Companion | The same model runs interactively in the Should-Cost dashboards (switchgear.html), with a 3D view and a month selector for the commodity prices.

## Inputs
LT board: specification and bay schedule
Tag / board name | LT-01 PCC 3200 A, 2 incomers + coupler
System voltage | 0.415 | kV (fixed)
Busbar rating | 3200 | A
Fault level (1 s) | 50 | kA
Degree of protection | IP54
Arc-fault protection (IAC) | No
Separation form | Form 4b
Busbar material | Aluminium
Bay schedule
Bay type | Quantity | Size | Unit
ACB incomer | 2 | 3200 | A
ACB bus coupler | 1 | 3200 | A
ACB outgoing feeder | 4 | 800 | A
MCCB feeder (each) | 12 | 250 | A
MCC starter, DOL | 0 | 15 | kW
MCC starter, star-delta | 0 | 55 | kW
MCC starter, VFD | 0 | 30 | kW
APFC bank | 0 | 200 | kVAr
Size: rated current (A) for breakers and feeders, motor kW for starters, kVAr for APFC banks. Quantity 0 removes a bay type.

## Summary
LT board: should-cost summary
LT-01 PCC 3200 A, 2 incomers + coupler
Cost group | Rs | Share | Note
Enclosure & structure | 313760.0717 | 4.804% | Sheet steel, pre-treatment, powder coat, doors
Busbars & insulation | 408256 | 6.251% | Main (and vertical) busbar, sleeving
Switching devices | 3285302.0327 | 50.3% | ACBs, MCCBs, starters, VFDs, APFC
Protection & metering | 576100 | 8.821% | CTs, VTs, relays, meters
Wiring & auxiliaries | 266500 | 4.08% | Control wiring, interlocks, lamps, selectors
Assembly, test, packing & transport | 597347.4425 | 9.146% | Labour, routine and type tests, packing
Direct cost | 5447265.5469 | 83.4%
Overheads | 490253.8992 | 7.506%
Margin | 593751.9446 | 9.091%
SHOULD-COST, ex-works (Rs) | 6531271.3907 | 100%
Should-cost (Rs crore) | 0.65313
Number of bays (units) | 19
Cost per bay (Rs) | 343751.1258
Cost per ampere of busbar (Rs/A) | 2041.0223
Sheet steel (kg) | 3120.128
Busbar mass (kg) | 864
Checks
Largest bay rating within the busbar rating? | OK
Fault level within the usual range? | OK

## Bay Costing
Cost per bay and board-level items
Rows follow the bay schedule on Inputs. Rs per bay unless stated.
Enclosure multiplier (IP x form x arc) |  |  |  | 1.408
Bay type | Qty | Size | Steel kg / bay | Sheet steel | Powder coat | Gaskets, doors | Device | Protection & metering | Aux + wiring | Total per bay | Total (qty x) | Columns
ACB incomer | 2 | 3200 | 450.56 | 34242.56 | 6307.84 | 4757.9136 | 747763.5444 | 60700 | 28300 | 882071.858 | 1764143.716 | 2
ACB bus coupler | 1 | 3200 | 450.56 | 34242.56 | 6307.84 | 4757.9136 | 747763.5444 | 60700 | 28300 | 882071.858 | 882071.858 | 1
ACB outgoing feeder | 4 | 800 | 281.6 | 21401.6 | 3942.4 | 2973.696 | 171790.9507 | 60700 | 28300 | 289108.6467 | 1156434.5867 | 4
MCCB feeder (each) | 12 | 250 | 53.504 | 4066.304 | 749.056 | 565.0022 | 29570.6331 | 12600 | 1950 | 49500.9953 | 594011.9437 | 3
MCC starter, DOL | 0 | 15 | 41.1647 | 3128.5177 | 576.3059 | 434.6993 | 12146.3895 | 22100 | 6500 | 44885.9123 | 0 | 0
MCC starter, star-delta | 0 | 55 | 54.639 | 4152.5658 | 764.9463 | 576.9881 | 42215.1356 | 22100 | 6500 | 76309.6358 | 0 | 0
MCC starter, VFD | 0 | 30 | 62.9486 | 4784.0971 | 881.281 | 664.7377 | 167143.5758 | 22100 | 6500 | 202073.6916 | 0 | 0
APFC bank | 0 | 200 | 295.68 | 22471.68 | 4139.52 | 3122.3808 | 192000 | 28000 | 6500 | 256233.5808 | 0 | 0
Board-level items
Item | Qty | Unit |  | Rate Rs |  |  |  | Amount Rs | Group
Main busbar (per busbar material) | 864 | kg |  | 444 |  |  |  | 383616 | Busbars & insulation
Vertical busbars, MCC sections | 0 | kg |  | 444 |  |  |  | 0 | Busbars & insulation
Busbar sleeving, supports and barriers | 80 | m |  | 308 |  |  |  | 24640 | Busbars & insulation
Arc-flash relay and sensors | 0 | set |  | 42500 |  |  |  | 0 | Wiring & auxiliaries
Earth bar, nameplates, end covers | 10 | column |  | 4500 |  |  |  | 45000 | Wiring & auxiliaries
Assembly, fabrication and wiring labour | 3120.128 | kg |  | 45.6 |  |  |  | 142277.8368 | Assembly & test
Routine tests, FAT and inspection | 19 | bay |  | 6500 |  |  |  | 123500 | Assembly & test
Type-test and certification allowance | 1 | lot |  | 96998.3621 |  |  |  | 96998.3621 | Assembly & test
Packing and transport | 1 | lot |  | 234571.2436 |  |  |  | 234571.2436 | Assembly & test
Helper figures
Number of bays (units) | 19
Columns / panels | 10
Board length m (columns x width) | 8
Busbar run length m (board + 1.2 m risers per column) | 20
Busbar section mm2 per phase | 4000
Sheet steel total kg | 3120.128

## Rates
Rates and constants
Blue = assumption. Replace with quotes. Each value is a named cell (r_...), so formulas stay readable.
Commodity rates
Copper (busbar) | 1400 | Rs/kg | Commodity file / LME x USDINR
Aluminium (busbar) | 349 | Rs/kg
CRCA sheet | 76 | Rs/kg
Switching devices
ACB base price at 1,000 A, 50 kA, 3-pole | 210000 | Rs
ACB rating exponent | 0.9
ACB fault-level exponent (kA/50) | 0.3
Factor for 4-pole (incomers, couplers) | 1.25 | x
MCCB price = base x A^exp x (kA/36)^exp | 80 | Rs
MCCB rating exponent | 1.05
MCCB fault-level exponent | 0.35
DOL starter base (MPCB, contactor, overload) | 3000 | Rs
DOL starter per kW^exp | 1200 | Rs
Starter kW exponent | 0.75
Star-delta factor | 1.55 | x
VFD = base x kW^exp | 11000 | Rs
VFD kW exponent | 0.8
APFC bank base (controller, switching) | 62000 | Rs
APFC capacitors and reactors per kVAr | 650 | Rs/kVAr
Protection, metering and accessories
CT (each) | 4800 | Rs
Microprocessor release / relay element | 9500 | Rs
Multi-function meter | 7500 | Rs
Ammeter / voltmeter set | 5500 | Rs
Indicating lamp | 1800 | Rs
Selector switch | 1200 | Rs
MCCB shunt trip / aux | 6000 | Rs
ACB shunt trip, closing coil, interlocks | 14000 | Rs
APFC controller, CTs and metering | 28000 | Rs
Sheet steel per bay (kg)
ACB bay: base | 160 | kg
ACB bay: per ampere | 0.05 | kg/A
MCCB feeder: base | 28 | kg
MCCB feeder: per ampere | 0.04 | kg/A
MCC module: base | 24 | kg
MCC module: per kW^0.8 | 0.6 | kg
VFD module factor | 1.35 | x
APFC bay: base | 120 | kg
APFC bay: per kVAr | 0.45 | kg
Busbar
Copper busbar section | 0.8 | mm2/A
Aluminium busbar section | 1.25 | mm2/A
MCC vertical busbar fraction of main | 0.5
Column width | 0.8 | m
Busbar fabrication, plating | 95 | Rs/kg
Sleeving, supports, barriers | 220 | Rs/m per phase
Form 4b sleeving factor | 1.4 | x
MCC modules per column | 8 | nos
MCCB feeders per column | 4 | nos
Control wiring and terminals | 6500 | Rs/bay
MCCB feeder wiring factor | 0.3 | x
Arc-flash relay and sensors (LT = 50%) | 85000 | Rs
Form 4b assembly factor | 1.2 | x
Enclosure multipliers
IP42 | 1
IP54 | 1.1
IP55 | 1.14
Form 2b | 1
Form 3b | 1.12
Form 4b | 1.28
Arc-proof (internal arc classified) enclosure | 1.2 | x
Shop floor, test and cost stack
Pre-treatment and powder coating | 14 | Rs/kg steel
Gaskets, doors, hardware | 6 | Rs/kg steel
Hardware as share of sheet price | 0.06 | x
Assembly, fabrication and wiring labour | 38 | Rs/kg steel
Routine tests, FAT and inspection | 6500 | Rs/bay
Type-test and certification allowance | 2% | of material
Earth bar, nameplates, end covers | 4500 | Rs/column
Packing | 2.5% | of ex-works
Transport to site | 2% | of ex-works
Overheads | 9% | of direct
Margin | 10% | of direct + overheads

## Presets
Sample boards (copy the values into Inputs)
Board | kV | Busbar A | kA
LT-01 PCC 3200 A, 2 incomers + coupler | 0.415 | 3200 | 50 | aci=2@3200; acc=1@3200; acf=4@800; mcf=12@250; dol=0; sd=0; vfd=0; pf=0 | IP54, Form 4b, Aluminium busbar
LT-02 MCC, 40 starters | 0.415 | 1000 | 50 | aci=1@1000; acc=0; acf=0; mcf=4@125; dol=28@11; sd=6@55; vfd=6@30; pf=0 | IP54, Form 3b, Copper busbar
LT-03 APFC panel 600 kVAr | 0.415 | 1000 | 36 | aci=1@1000; acc=0; acf=0; mcf=0; dol=0; sd=0; vfd=0; pf=3@200 | IP42, Form 2b, Aluminium busbar