## Read Me
Cooling tower: should-cost model
Thermal sizing (Merkel number) and bottom-up costing of a mechanical or natural-draught cooling tower. Not a vendor price list: every rate is an editable assumption.
Purpose | Estimate the ex-works price of a cooling tower from heat load, range, approach and design wet-bulb. The thermal duty sets the water flow; the Merkel number demanded by range, approach and wet-bulb sets the fill depth; the liquid-to-air ratio is chosen to give the cheapest fill-plus-fan combination; quantities then follow and are priced.
How to use | Edit the yellow cells on Inputs (duty and tower type) and, if you have quotes, on Rates. Everything else is a live formula. Results are on Summary. The L/G scan is on Thermal; the priced build-up is on Costing.
Sheets | Inputs: duty and type. Summary: key results, cost stack, per-TR and per-m3/h figures, benchmark check. Thermal: psychrometrics, Merkel integral and the L/G scan. Costing: geometry, quantities, rates and amounts. Rates: tower-type table, fill rates and every price and constant (named cells r_...). Presets: five sample towers.
Method | Merkel number by the four-point Chebyshev integral of 1/(h_sat - h_air) at 10, 40, 60 and 90% of the range. Fill characteristic KaV/L = c x (L/G)^-n per metre of fill, so depth = Merkel / (c x (L/G)^-n), clamped between the minimum and 2.2 x the maximum depth on Rates. The L/G scan runs from the minimum to the maximum on Rates in steps of 0.05.
Conventions | Yellow fill = input. Blue font = a typed assumption you may change. Black = formula. Green fill = key output. Amounts in Indian rupees, ex-GST, ex-works.
Reasonableness | At the default rates: FRP counterflow about Rs 4,700-5,200 per TR, HDG steel about Rs 3,000, RCC power-plant towers about Rs 1,900, small crossflow about Rs 6,500. The fill characteristic constants (c, n) are generic, not a vendor’s fill data: replace them with the manufacturer’s curves before relying on the fill depth.
Limits | An approach below 2.8 K is not practical for a mechanical-draught tower and is flagged. Hot-water basin, pumps, piping, civil basin and electrical supply are excluded. Make-up water is shown, not costed.
Companion | The same model runs in the Should-Cost dashboards (cooling-towers.html), with a section view, a 3D model and a month selector for steel prices.

## Inputs
Cooling tower: duty and type
Tag / tower name | CT-01 1,000 TR chiller plant (FRP)
Heat rejected | 3517 | kW | 1000
Range (hot water - cold water) | 5 | K
Approach (cold water - wet-bulb) | 4 | K
Design wet-bulb | 28 | °C
Tower type | Counterflow, induced draught, FRP |  | pick from list
Fan drive | No |  | No = direct on line, Yes = VFD

## Summary
Cooling tower: should-cost summary
CT-01 1,000 TR chiller plant (FRP) |  | OK
Cost group | Rs | Share | Note
Fill & drift | 1667068.7603 | 32.57% | Fill pack, eliminators, distribution
Casing, structure & basin | 999830.8327 | 19.53% | Casing or shell, basin, louvres
Fans & drives | 918235.1223 | 17.94% | Fans, gearboxes, motors, VFDs
Accessories | 118000 | 2.305% | Ladders, controls, vibration switches
Assembly & supply | 685079.9223 | 13.38% | Erection and assembly labour, transport
Overheads | 351057.171 | 6.859%
Margin | 379141.7447 | 7.407%
SHOULD-COST, ex-works (Rs) | 5118413.5533 | 100%
Check against Costing sheet | OK
Key results
Should-cost (Rs crore) | 0.51184
Rs per TR | 5118.4136
Rs per m3/h of water | 8462.7736
Heat rejected (TR) | 1000
Water flow (m3/h) | 604.8151
Hot / cold water (°C) | 37.0 / 32.0
L/G ratio chosen | 1.3
Merkel number demanded | 0.92371
Fill depth (m) | 1.0351
Plan area (m2) | 43.2011
Cells x cell side (m) | 1 x 6.6 m
Height (m) | 3.9351
Fan shaft power, total (kW) | 27.1881
Motor per cell (kW) | 31.5
Fan diameter (m) | 4.4579
Make-up water (m3/h) | 4.6268
Benchmark
Band for this type, Rs per TR | 4,200 - 7,000
This tower against the band | inside
Approach check | OK

## Thermal
Thermal sizing
Duty, psychrometrics, Merkel integral and the L/G scan.
Status | OK
Cold water out | 32
Hot water in | 37
Water flow m3/h | 604.8151
Tower type row | 1
Fill characteristic c | 1.05
Fill exponent n | 0.62
Plan loading m3/h per m2 | 14
Natural draught? | 0
Plan area m2 | 43.2011
Air enthalpy at wet-bulb (kJ/kg) | 89.7025
Chebyshev points
Point (fraction of range) | x | Water temp | Saturated enthalpy
Point 1 | 0.1 | 32.5 | 113.4944
Point 2 | 0.4 | 34 | 122.5706
Point 3 | 0.6 | 35 | 128.9813
Point 4 | 0.9 | 36.5 | 139.1777
L/G scan
Step | L/G | Valid? | Sum 1/(hs - h) | Merkel demand | KaV/L per m | Fill depth m | Air kg/s | Air m3/s | Fan shaft kW | Cost proxy Rs | Fill m3
0 | 0.9 | 1 | 0.15161 | 0.79331 | 1.1209 | 0.70775 | 186.6713 | 162.3229 | 39.2717 | 3304147.2259 | 30.5757
1 | 0.95 | 1 | 0.15423 | 0.80702 | 1.0839 | 0.74453 | 176.8465 | 153.7796 | 37.2047 | 3229381.5113 | 32.1644
2 | 1 | 1 | 0.15697 | 0.82135 | 1.05 | 0.78224 | 168.0042 | 146.0906 | 35.3445 | 3168270.9081 | 33.7936
3 | 1.05 | 1 | 0.15984 | 0.83636 | 1.0187 | 0.821 | 160.004 | 139.1339 | 33.6614 | 3119194.6572 | 35.468
4 | 1.1 | 1 | 0.16285 | 0.8521 | 0.98975 | 0.86093 | 152.7311 | 132.8096 | 32.1314 | 3080864.2943 | 37.193
5 | 1.15 | 1 | 0.16601 | 0.86864 | 0.96285 | 0.90215 | 146.0906 | 127.0353 | 30.7344 | 3052256.1909 | 38.974
6 | 1.2 | 1 | 0.16933 | 0.88603 | 0.93777 | 0.94482 | 140.0035 | 121.7422 | 29.4538 | 3032561.8868 | 40.8173
7 | 1.25 | 1 | 0.17283 | 0.90435 | 0.91433 | 0.98908 | 134.4034 | 116.8725 | 28.2756 | 3021151.4328 | 42.7295
8 | 1.3 | 1 | 0.17653 | 0.92371 | 0.89237 | 1.0351 | 129.234 | 112.3774 | 27.1881 | 3017546.4824 | 44.7181
9 | 1.35 | 1 | 0.18044 | 0.94418 | 0.87173 | 1.0831 | 124.4476 | 108.2153 | 26.1811 | 3021400.9149 | 46.7914
10 | 1.4 | 1 | 0.18459 | 0.96589 | 0.85229 | 1.1333 | 120.003 | 104.3504 | 25.2461 | 3032487.4952 | 48.9588
11 | 1.45 | 1 | 0.189 | 0.98896 | 0.83395 | 1.1859 | 115.865 | 100.7521 | 24.3755 | 3050689.6121 | 51.2309
12 | 1.5 | 1 | 0.1937 | 1.0135 | 0.81661 | 1.2412 | 112.0028 | 97.3937 | 23.563 | 3075997.5559 | 53.6199
13 | 1.55 | 1 | 0.19872 | 1.0398 | 0.80017 | 1.2995 | 108.3898 | 94.252 | 22.8029 | 3108509.1565 | 56.1398
14 | 1.6 | 1 | 0.20411 | 1.068 | 0.78458 | 1.3612 | 105.0026 | 91.3066 | 22.0903 | 3148434.9536 | 58.807
15 | 1.65 | 1 | 0.2099 | 1.0983 | 0.76975 | 1.4268 | 101.8207 | 88.5398 | 21.4209 | 3196108.4594 | 61.6404
16 | 1.7 | 1 | 0.21615 | 1.131 | 0.75563 | 1.4968 | 98.826 | 85.9357 | 20.7909 | 3252002.553 | 64.6629
17 | 1.75 | 1 | 0.22294 | 1.1665 | 0.74217 | 1.5718 | 96.0024 | 83.4803 | 20.1969 | 3316753.7027 | 67.9014
18 | 1.8 | 1 | 0.23033 | 1.2052 | 0.72932 | 1.6525 | 93.3357 | 81.1615 | 19.6358 | 3391196.663 | 71.3886
19 | 1.85 | 1 | 0.23843 | 1.2476 | 0.71704 | 1.7399 | 90.8131 | 78.9679 | 19.1051 | 3476413.7502 | 75.1647
20 | 1.9 | 1 | 0.24735 | 1.2943 | 0.70528 | 1.8351 | 88.4233 | 76.8898 | 18.6024 | 3573805.1045 | 79.2794
21 | 1.95 | 1 | 0.25727 | 1.3462 | 0.69401 | 1.9397 | 86.156 | 74.9183 | 18.1254 | 3685190.1508 | 83.7957
22 | 2 | 1 | 0.26837 | 1.4042 | 0.6832 | 2.0554 | 84.0021 | 73.0453 | 17.6723 | 3812956.9357 | 88.7943
23 | 2.05 | 1 | 0.28092 | 1.4699 | 0.67282 | 2.1847 | 81.9533 | 71.2637 | 17.2412 | 3960287.4796 | 94.3811
24 | 2.1 | 1 | 0.29528 | 1.5451 | 0.66285 | 2.3309 | 80.002 | 69.567 | 16.8307 | 4131508.4244 | 100.6989
Selected L/G
Best step (first minimum cost) | 9
L/G | 1.3
Merkel demand | 0.92371
Fill depth before clamping m | 1.0351
Fill depth used m | 1.0351
Air m3/s | 112.3774
Fan shaft kW (total) | 27.1881
Fill volume m3 | 44.7181

## Costing
Geometry and priced build-up
Quantities from the thermal sizing; rates from Rates.
Number of cells | 1
Plan area per cell m2 | 43.2011
Cell side m | 6.5728
Height m | 3.9351
Motor per cell kW | 31.5
Fan diameter m | 4.4579
Perimeter m (all cells) | 26.291
Louvre face m2 | 42.9888
Casing | FRP
Fill | Film PVC
Item | Qty | Unit | Rate Rs | Amount Rs | Group
Fill, installed | 44.7181 | m3 | 31000 | 1386261.7341 | Fill & drift
Drift eliminators | 43.2011 | m2 | 2300 | 99362.4862 | Fill & drift
Water distribution headers and nozzles | 43.2011 | m2 | 4200 | 181444.54 | Fill & drift
FRP casing, panels and framing | 146.6593 | m2 | 5200 | 762628.1301 | Casing, structure & basin
Cold-water basin, FRP | 43.2011 | m2 | 3600 | 155523.8914 | Casing, structure & basin
Hot-dip galvanised structure and casing | 0 | kg | 108 | 0 | Casing, structure & basin
Steel basin and sheeting | 0 | kg | 97.2 | 0 | Casing, structure & basin
RCC shell, columns, fan deck and basin | 0 | m3 | 9800 | 0 | Casing, structure & basin
Air-inlet louvres | 42.9888 | m2 | 1900 | 81678.8112 | Casing, structure & basin
Axial fans (each) | 1 | nos | 618985.1223 | 618985.1223 | Fans & drives
Gearbox and drive shaft | 31.5 | kW | 5200 | 163800 | Fans & drives
Fan motors, IE3 | 31.5 | kW | 4300 | 135450 | Fans & drives
VFDs | 0 | kW | 7500 | 0 | Fans & drives
Ladders, handrails, level and make-up controls | 1 | cells | 90000 | 90000 | Accessories
Vibration switches | 1 | nos | 28000 | 28000 | Accessories
Material subtotal |  |  |  | 3703134.7153
Erection and assembly labour | 1 | lot | 592501.5544 | 592501.5544 | Assembly & supply
Transport to site | 1 | lot | 92578.3679 | 92578.3679 | Assembly & supply
Direct cost |  |  |  | 4388214.6376
Overheads |  |  |  | 351057.171
Margin |  |  |  | 379141.7447
SHOULD-COST, ex-works (Rs) |  |  |  | 5118413.5533

## Rates
Rates and constants
Blue = assumption. Each value is a named cell (r_...).
Tower types
Type | Fill | c (KaV/L per m) | n | Loading m3/h per m2 | Fan dP Pa | Casing | Max cell m3/h | Natural (1)
Counterflow, induced draught, FRP | Film PVC | 1.05 | 0.62 | 14 | 150 | FRP | 700 | 0
Crossflow, induced draught, FRP | Splash / low-clog film | 0.8 | 0.58 | 12 | 110 | FRP | 600 | 0
Counterflow, induced draught, RCC | Film PVC | 1.05 | 0.62 | 14 | 150 | RCC | 3500 | 0
Counterflow, induced draught, HDG steel | Film PVC | 1.05 | 0.62 | 14 | 150 | HDG steel | 1200 | 0
Natural draught, hyperbolic (RCC) | Film PVC | 1 | 0.6 | 10 | 0 | RCC | 60000 | 1
Fill rates, installed
Film PVC | 31000 | Rs/m3
Splash / low-clog film | 17000 | Rs/m3
Psychrometrics and L/G scan
Barometric pressure | 101.325 | kPa
L/G scan minimum | 0.9
L/G scan maximum | 2.1
L/G step | 0.05
Specific heat of water | 4.186 | kJ/kg K
Heat to flow: kW per (m3/h x K) | 1.163
Air density at fan | 1.15 | kg/m3
Maximum Merkel number considered | 25
Minimum fill depth | 0.9 | m
Maximum fill depth | 1.8 | m
Clamp multiple of maximum depth | 2.2 | x
Fan cost proxy in the L/G choice | 60000 | Rs per shaft kW
Fill, drift and distribution
Drift eliminators | 2300 | Rs/m2 plan
Water distribution headers and nozzles | 4200 | Rs/m2 plan
Air-inlet louvres | 1900 | Rs/m2 face
Louvre height beyond fill depth | 0.6 | m
Casing, structure and basin
FRP casing, panels, framing | 5200 | Rs/m2
Cold-water basin, FRP | 3600 | Rs/m2 plan
Hot-dip galvanised steel | 108 | Rs/kg
Steel per m2 plan at 8 m height | 85 | kg/m2
Reference height for steel | 8 | m
Steel basin and sheeting | 70 | kg/m2 plan
Basin steel price factor | 0.9 | x
RCC | 9800 | Rs/m3
RCC per m2 plan | 0.55 | m3/m2
Natural-draught shell factor | 3.2 | x
Height: distribution, plenum and basin | 2.1 | m
Height: fan stack (mechanical) | 0.8 | m
Height: extra for RCC | 1 | m
Fans and drives
Fan efficiency | 0.62
Fan face velocity | 7.2 | m/s
Fan cost: base | 42000 | Rs
Fan cost: diameter exponent | 1.8
Motor margin on shaft kW | 1.15 | x
Gearbox and drive shaft | 5200 | Rs/kW
Fan motors, IE3 | 4300 | Rs/kW
VFDs | 7500 | Rs/kW
Accessories and cost stack
Ladders, handrails, level and make-up controls | 90000 | Rs/cell
Vibration switch | 28000 | Rs/cell
Erection and assembly labour | 16% | of material
Transport to site | 2.5% | of material
Overheads | 8% | of direct
Margin | 8% | of direct + overheads
Make-up water factor | 0.00153 | m3/h per (m3/h x K)
Benchmark bands, Rs per TR
Type | Low | High
Counterflow, induced draught, FRP | 4200 | 7000
Crossflow, induced draught, FRP | 4500 | 7500
Counterflow, induced draught, RCC | 1500 | 2800
Counterflow, induced draught, HDG steel | 2400 | 4200
Natural draught, hyperbolic (RCC) | 1200 | 2500

## Presets
Sample towers (copy the values into Inputs)
Tower | kW | Range K | Approach K | Wet-bulb | Type | VFD
CT-01 1,000 TR chiller plant (FRP) | 3517 | 5 | 4 | 28 | Counterflow, induced draught, FRP | No
CT-02 3,000 TR plant (FRP, VFD) | 10551 | 5 | 4 | 28 | Counterflow, induced draught, FRP | Yes
CT-03 Process, steel (HDG) | 6000 | 8 | 5 | 27 | Counterflow, induced draught, HDG steel | No
CT-04 Power plant, RCC | 60000 | 10 | 7 | 28 | Counterflow, induced draught, RCC | No
CT-05 Small crossflow (FRP) | 800 | 5 | 4.5 | 28 | Crossflow, induced draught, FRP | No