## Read Me
Cable tray structural check
Strength, shear and deflection of ladder, perforated and trough trays, trapeze channels and cantilever arms. Standalone, formula-driven.
Purpose | Check whether a cable tray, a trapeze channel or a cantilever arm carries a given cable load over a given support spacing, and find the safe working load (SWL) and the longest span that still carries the load.
How to use | Enter one tray per row on Inputs (yellow cells): type, width, depth, steel thickness, the cable load in kg/m, the support span in m, the support condition and the concentrated load. Calc does the work row by row. Summary shows one row in detail (change the row number in its yellow cell), the verdict for every row, and a chart of SWL against span.
Method | 1) Section: thin-wall rectangular parts give area, neutral axis, second moment I and section moduli (perforation holes reduce the base plate of perforated and trough trays). 2) Straight tray or channel as a beam: bending M = kw·w·L² + kp·P·L, shear V = kv·(w·L + P), deflection d = dw·w·L⁴/EI + dp·P·L³/EI, with coefficients for a simple or a continuous span; the moment capacity is allowable stress × the smaller section modulus × a splice efficiency for the coupler joint. 3) Ladder rungs are checked separately as simply supported beams across the width. 4) Cantilever arm: the cable and tray load of one support spacing acts at mid-length of the arm plus an installer load at the tip, checked for bending, shear and tip deflection (limit = arm length / 100). 5) SWL is the cable load at which the first of bending, shear or deflection governs, after deducting the tray self-weight.
Verdict | PASS when every utilisation (applied ÷ capacity) is at most 100%. The governing check is the one with the smallest SWL.
Self-weight | Type the tray weight in kg/m if you know it (for example from the cost model or a catalogue). Leave it blank to use the estimate computed from the section area and, for ladders, the rungs.
Conventions | Yellow fill = input. Blue font = a typed assumption (Parameters). Black = formula. Green fill = key output. Units: mm, N and MPa inside the calculation; kg, kg/m and m on the sheets that you read.
Origin | This workbook mirrors the structural check in the Should-Cost dashboards (cable-trays.html, tab Structural check) and reproduces its results; the dashboard model is an own calculation, not taken from a vendor or code workbook. The sample rows on Inputs are the cases used to verify the workbook against the dashboard.
Limits | Elastic design with a single factor of safety on yield; no web-crippling, lateral-torsional or local-buckling design (slenderness flags only); no seismic or wind load; fittings (bends, tees, crosses) are not checked here: check the straight tray they connect to and keep their support spacing to about half the straight-run span. This is a screening check, not a certified design: confirm against the manufacturer's load-span table or NEMA VE 1 / IEC 61537 type test data before relying on it.

## Inputs
Inputs: one tray per row
Yellow cells are inputs. Kinds: ladder, perf (perforated), trough, channel, arm (cantilever arm). Clear a row's Kind to leave it out.
Tag | Kind | Width | Depth | Thickness | Arm length | Self-weight (blank = estimate) | Cable load | Support span / arm spacing | Support | Point load | Deflection limit | Channel span | Supported tray weight
|  | mm | mm | mm | mm (arm) | kg/m | kg/m | m | simple / continuous | kg | L / x | mm (channel) | kg/m (arm, channel)
Ladder 600 x 100 x 2.0, simple span | ladder | 600 | 100 | 2 |  | 8.56 | 40 | 2.5 | simple | 90 | 200
Ladder 300 x 75 x 2.0, continuous | ladder | 300 | 75 | 2 |  | 6.079 | 30 | 3 | continuous | 90 | 200
Ladder 600 x 100 x 2.0, overloaded | ladder | 600 | 100 | 2 |  | 8.56 | 400 | 2.5 | simple | 90 | 200
Perforated 300 x 100 x 2.0 | perf | 300 | 100 | 2 |  | 9.028 | 25 | 2 | simple | 90 | 200
Trough 150 x 50 x 2.5 | trough | 150 | 50 | 2.5 |  | 5.403 | 10 | 1.5 | simple | 60 | 200
Cantilever arm 620 mm, 41 x 41 x 2.5 | arm | 41 | 41 | 2.5 | 620 | 2.796 | 20 | 2 | simple | 90 | 200 |  | 8
Cantilever arm 320 mm, 41 x 41 x 2.5 | arm | 41 | 41 | 2.5 | 320 | 2.8 | 20 | 2 | simple | 90 | 200 |  | 8
Channel 41 x 41 x 2.5, trapeze 600 mm | channel | 41 | 41 | 2.5 |  | 2.791 | 20 | 2 | simple | 90 | 200 | 600 | 8
Arm: enter the arm length in "Arm length", the arm spacing along the run in "Support span / arm spacing", and the weight of tray supported per metre in the last column.
Channel: the channel span is the trapeze length between its two hangers; the cable and tray load of one support spacing acts on it as a uniform load.
Straight tray (ladder, perf, trough): "Support span" is the distance between supports; support condition simple or continuous over several spans.

## Summary
Summary
Pick a row to see it in detail. The table below lists every row.
Row to show (1-20) | 1
Tray
Tag | Ladder 600 x 100 x 2.0, simple span
Kind | ladder
Width x depth x thickness (mm) | 600 x 100 x 2
Cable load | 40 | kg/m
Support span / arm spacing | 2.5 | m
Result
VERDICT | PASS
Safe working load | 94.2507 | kg/m
Governing check | bending
Governing utilisation | 81.91%
Load margin (SWL / load - 1) | 135.6%
Safe working load per arm | n/a | kg
Utilisation (applied / capacity)
Bending | 68.97%
Shear in the webs | 2.592%
Deflection | 26.04%
Rung bending (ladder) | 81.91%
Section
Section area | 600 | mm²
Neutral axis from base | 50 | mm
Second moment I | 813600 | mm⁴
Section modulus, base | 16272 | mm³
Section modulus, top | 16272 | mm³
Self-weight used | 8.56 | kg/m
Slenderness flags
Longest span that carries the load | 3.2404 | m
Resolution 0.1 m with linear interpolation between grid points. Channels have no span curve (the channel span is fixed).
Row / tag | Kind | SWL kg/m | Load kg/m | Utilisation | Governing | Verdict
1 Ladder 600 x 100 x 2.0, simple span | ladder | 94.2507 | 40 | 81.91% | bending | PASS
2 Ladder 300 x 75 x 2.0, continuous | ladder | 35.1696 | 30 | 94.89% | bending | PASS
3 Ladder 600 x 100 x 2.0, overloaded | ladder | 94.2507 | 400 | 274.9% | bending | FAIL
4 Perforated 300 x 100 x 2.0 | perf | 181.0628 | 25 | 44.28% | bending | PASS
5 Trough 150 x 50 x 2.5 | trough | 18.0657 | 10 | 92.2% | bending | PASS
6 Cantilever arm 620 mm, 41 x 41 x 2.5 | arm | 45.2674 | 20 | 69.66% | bending | PASS
7 Cantilever arm 320 mm, 41 x 41 x 2.5 | arm | 123.3305 | 20 | 35.95% | bending | PASS
8 Channel 41 x 41 x 2.5, trapeze 600 mm | channel | 328.1907 | 20 | 62.78% | bending | PASS

## Calc
Calculation: one row per tray
Same row numbers as Inputs. Section (1), beam check (2), arm check (3), result (4).
Tag | Kind | Perforation ratio | Return width | Part 1 area | Part 1 centroid | Part 1 own I | Part 2 area | Part 2 centroid | Part 2 own I | Part 3 area | Part 3 centroid | Part 3 own I | Section area | Neutral axis from base | Second moment I | Z, base | Z, top | Web area | Self-weight estimate | Self-weight used | Web depth / t | Return / t | Base width / t | Slenderness flags | kw | kp | dw | dp | kv | Allowable stress | Point load | EI | Shear capacity | Beam span L | Cable line load | Moment capacity (beam) | Deflection limit | Self load | Cable load | Applied moment | Applied shear | Deflection | SWL, bending | SWL, shear | SWL, deflection | SWL (beam) | Governing (beam) | Rung utilisation | Moment capacity (arm) | Tip deflection limit | Cable load on one arm | Cable + tray on one arm | Tip load | Applied moment | Applied shear | Tip deflection | Arm capacity, bending | Arm capacity, shear | Arm capacity, deflection | SWL per arm | SWL (arm) | Governing (arm) | Moment capacity | Applied moment | Applied shear | Deflection | Deflection limit | Bending utilisation | Shear utilisation | Deflection utilisation | Governing utilisation | SAFE WORKING LOAD | Governing check | VERDICT | Load margin
|  |  | mm | mm² | mm | mm⁴ | mm² | mm | mm⁴ | mm² | mm | mm⁴ | mm² | mm | mm⁴ | mm³ | mm³ | mm² | kg/m | kg/m | [9 empty] | MPa | N | N·mm² | N | mm | kg/m | N·mm | mm | N/mm | N/mm | N·mm | N | mm | kg/m | kg/m | kg/m | kg/m |  |  | N·mm | mm | N | N | N | N·mm | N | mm | kg | kg | kg | kg | kg/m |  | N·mm | N·mm | N | mm | mm |  |  |  |  | kg/m |  |  | %
Ladder 600 x 100 x 2.0, simple span | ladder | 0 | 25 | 400 | 50 | 333333.3333 | 100 | 1 | 33.3333 | 100 | 99 | 33.3333 | 600 | 50 | 813600 | 16272 | 16272 | 400 | 8.1012 | 8.56 | 50 | 12.5 | 0 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 882.9 | 162720000000 | 40000 | 2500 | 40 | 1339760.479 | 12.5 | 0.083974 | 0.3924 | 923979.375 | 1036.917 | 3.2553 | 94.2507 | 3217.4176 | 341.4859 | 94.2507 | bending | 0.81913 | [14 empty] | 1339760.479 | 923979.375 | 1036.917 | 3.2553 | 12.5 | 0.68966 | 0.025923 | 0.26042 | 0.81913 | 94.2507 | bending | PASS | 135.6%
Ladder 300 x 75 x 2.0, continuous | ladder | 0 | 25 | 300 | 37.5 | 140625 | 100 | 1 | 33.3333 | 100 | 74 | 33.3333 | 500 | 37.5 | 407141.6667 | 10857.1111 | 10857.1111 | 300 | 5.6206 | 6.079 | 37.5 | 12.5 | 0 |  | 0.1 | 0.2 | 0.0068966 | 0.009434 | 0.6 | 149.7006 | 882.9 | 81428333333.3333 | 30000 | 3000 | 30 | 893923.819 | 15 | 0.059635 | 0.2943 | 848281.491 | 1166.823 | 5.1899 | 35.1696 | 1662.8677 | 175.7682 | 35.1696 | bending | 0.39494 | [14 empty] | 893923.819 | 848281.491 | 1166.823 | 5.1899 | 15 | 0.94894 | 0.038894 | 0.34599 | 0.94894 | 35.1696 | bending | PASS | 17.23%
Ladder 600 x 100 x 2.0, overloaded | ladder | 0 | 25 | 400 | 50 | 333333.3333 | 100 | 1 | 33.3333 | 100 | 99 | 33.3333 | 600 | 50 | 813600 | 16272 | 16272 | 400 | 8.1012 | 8.56 | 50 | 12.5 | 0 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 882.9 | 162720000000 | 40000 | 2500 | 400 | 1339760.479 | 12.5 | 0.083974 | 3.924 | 3683041.875 | 5451.417 | 14.2943 | 94.2507 | 3217.4176 | 341.4859 | 94.2507 | bending | 1.8723 | [14 empty] | 1339760.479 | 3683041.875 | 5451.417 | 14.2943 | 12.5 | 2.749 | 0.13629 | 1.1435 | 2.749 | 94.2507 | bending | FAIL | -76.44%
Perforated 300 x 100 x 2.0 | perf | 0.066667 | 15 | 567.4667 | 1 | 0 | 400 | 50 | 333333.3333 | 60 | 99 | 20 | 1027.4667 | 25.7989 | 1238118.4307 | 47991.2107 | 16685.9754 | 400 | 8.0656 | 9.028 | 50 | 7.5 | 152 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 882.9 | 247623686132.018 | 40000 | 2000 | 25 | 1373845.2812 | 10 | 0.088565 | 0.24525 | 608357.34 | 775.2647 | 0.8751 | 181.0628 | 4023.444 | 1130.5864 | 181.0628 | bending | [15 empty] | 1373845.2812 | 608357.34 | 775.2647 | 0.8751 | 10 | 0.44281 | 0.019382 | 0.08751 | 0.44281 | 181.0628 | bending | PASS | 624.3%
Trough 150 x 50 x 2.5 | trough | 0.066667 | 0 | 359.3333 | 1.25 | 0 | 250 | 25 | 52083.3333 | 0 | 48.75 | 0 | 609.3333 | 10.9943 | 135242.4382 | 12301.1906 | 3467.2442 | 250 | 4.7833 | 5.403 | 20 | 0 | 61.6 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 588.6 | 27048487645.8789 | 25000 | 1500 | 10 | 285476.6902 | 7.5 | 0.053003 | 0.0981 | 263222.8397 | 407.6276 | 1.8983 | 18.0657 | 3352.4903 | 244.3092 | 18.0657 | bending | [15 empty] | 285476.6902 | 263222.8397 | 407.6276 | 1.8983 | 7.5 | 0.92205 | 0.016305 | 0.25311 | 0.92205 | 18.0657 | bending | PASS | 80.66%
Cantilever arm 620 mm, 41 x 41 x 2.5 | arm | 0 | 9 | 102.5 | 1.25 | 53.3854 | 205 | 20.5 | 28717.0833 | 45 | 39.75 | 23.4375 | 352.5 | 17.3599 | 79976.209 | 4606.9433 | 3383.0782 | 205 | 2.7671 | 2.796 | 16.4 | 3.6 | 16.4 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 882.9 | 15995241799.6454 | 20500 | 2000 | 20 | 278546.8592 | 10 | 0.027429 | 0.1962 | 553264.38 | 665.0788 | 12.1123 | 0 | 2041.9084 | 3.4682 | 0 | bending |  | 506448.835 | 6.2 | 392.4 | 549.36 | 294.3 | 352767.6 | 843.66 | 2.4849 | 90.5348 | 2043.7044 | 243.3348 | 90.5348 | 45.2674 | bending | 506448.835 | 352767.6 | 843.66 | 2.4849 | 6.2 | 0.69655 | 0.041154 | 0.40078 | 0.69655 | 45.2674 | bending | PASS | 126.3%
Cantilever arm 320 mm, 41 x 41 x 2.5 | arm | 0 | 9 | 102.5 | 1.25 | 53.3854 | 205 | 20.5 | 28717.0833 | 45 | 39.75 | 23.4375 | 352.5 | 17.3599 | 79976.209 | 4606.9433 | 3383.0782 | 205 | 2.7671 | 2.8 | 16.4 | 3.6 | 16.4 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 882.9 | 15995241799.6454 | 20500 | 2000 | 20 | 278546.8592 | 10 | 0.027468 | 0.1962 | 553284 | 665.118 | 12.1128 | 0 | 2041.9044 | 3.4642 | 0 | bending |  | 506448.835 | 3.2 | 392.4 | 549.36 | 294.3 | 182073.6 | 843.66 | 0.34165 | 246.6611 | 2043.7044 | 1177.8311 | 246.6611 | 123.3305 | bending | 506448.835 | 182073.6 | 843.66 | 0.34165 | 3.2 | 0.35951 | 0.041154 | 0.10676 | 0.35951 | 123.3305 | bending | PASS | 516.7%
Channel 41 x 41 x 2.5, trapeze 600 mm | channel | 0 | 9 | 102.5 | 1.25 | 53.3854 | 205 | 20.5 | 28717.0833 | 45 | 39.75 | 23.4375 | 352.5 | 17.3599 | 79976.209 | 4606.9433 | 3383.0782 | 205 | 2.7671 | 2.791 | 16.4 | 3.6 | 16.4 |  | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5 | 149.7006 | 882.9 | 15995241799.6454 | 20500 | 600 | 93.3333 | 278546.8592 | 3 | 0.02738 | 0.9156 | 174869.0869 | 724.3439 | 0.34787 | 328.1907 | 6812.8903 | 2655.8823 | 328.1907 | bending | [15 empty] | 278546.8592 | 174869.0869 | 724.3439 | 0.34787 | 3 | 0.62779 | 0.035334 | 0.11596 | 0.62779 | 328.1907 | bending | PASS | 1541%

## Span curve
Safe working load against span (row selected on Summary)
Straight trays and arms. For an arm the "span" is the arm spacing along the run.
Kind | ladder
Cable load (kg/m) | 40
Result
Longest span carrying the load (m) | 3.2404
Note
Selected row (helper values)
Span (m) | SWL (kg/m) | Load (kg/m) | Carries load? | kind | ladder
0.5 | 4001.7086 | 40 | yes | load | 40
0.6 | 2726.3488 | 40 | yes | pt | 90
0.7 | 1964.026 | 40 | yes | defl | 200
0.8 | 1473.5762 | 40 | yes | trayKg | 0
0.9 | 1140.2883 | 40 | yes | La | 0
1 | 904.0072 | 40 | yes | kw | 0.125
1.1 | 730.7517 | 40 | yes | kp | 0.25
1.2 | 600.1672 | 40 | yes | dw | 0.013021
1.3 | 499.4679 | 40 | yes | dp | 0.020833
1.4 | 420.3008 | 40 | yes | kv | 0.5
1.5 | 357.0254 | 40 | yes | sigma | 149.7006
1.6 | 305.724 | 40 | yes | P | 882.9
1.7 | 263.6086 | 40 | yes | EI | 162720000000
1.8 | 228.6521 | 40 | yes | Vall | 40000
1.9 | 199.3533 | 40 | yes | Mallb | 1339760.479
2 | 174.5818 | 40 | yes | Malla
2.1 | 153.4734 | 40 | yes | self | 8.56
2.2 | 135.3588 | 40 | yes | wS | 0.083974
2.3 | 119.7136 | 40 | yes
2.4 | 106.1218 | 40 | yes
2.5 | 94.2507 | 40 | yes
2.6 | 83.8316 | 40 | yes
2.7 | 74.6454 | 40 | yes
2.8 | 66.5123 | 40 | yes
2.9 | 59.2839 | 40 | yes
3 | 52.8364 | 40 | yes
3.1 | 47.0661 | 40 | yes
3.2 | 41.886 | 40 | yes
3.3 | 37.2221 | 40 | no
3.4 | 33.0116 | 40 | no
3.5 | 29.2006 | 40 | no
3.6 | 25.743 | 40 | no
3.7 | 22.599 | 40 | no
3.8 | 19.7341 | 40 | no
3.9 | 17.1183 | 40 | no
4 | 14.7254 | 40 | no
4.1 | 12.5326 | 40 | no
4.2 | 10.5198 | 40 | no
4.3 | 8.6692 | 40 | no
4.4 | 6.9652 | 40 | no
4.5 | 5.3939 | 40 | no
4.6 | 3.9432 | 40 | no
4.7 | 2.6019 | 40 | no
4.8 | 1.3604 | 40 | no
4.9 | 0.20998 | 40 | no
5 | 0 | 40 | no
5.1 | 0 | 40 | no
5.2 | 0 | 40 | no
5.3 | 0 | 40 | no
5.4 | 0 | 40 | no
5.5 | 0 | 40 | no
5.6 | 0 | 40 | no
5.7 | 0 | 40 | no
5.8 | 0 | 40 | no
5.9 | 0 | 40 | no
6 | 0 | 40 | no
6.1 | 0 | 40 | no
6.2 | 0 | 40 | no
6.3 | 0 | 40 | no
6.4 | 0 | 40 | no
6.5 | 0 | 40 | no
6.6 | 0 | 40 | no
6.7 | 0 | 40 | no
6.8 | 0 | 40 | no
6.9 | 0 | 40 | no
7 | 0 | 40 | no
7.1 | 0 | 40 | no
7.2 | 0 | 40 | no
7.3 | 0 | 40 | no
7.4 | 0 | 40 | no
7.5 | 0 | 40 | no
7.6 | 0 | 40 | no
7.7 | 0 | 40 | no
7.8 | 0 | 40 | no
7.9 | 0 | 40 | no
8 | 0 | 40 | no
8.1 | 0 | 40 | no
8.2 | 0 | 40 | no
8.3 | 0 | 40 | no
8.4 | 0 | 40 | no
8.5 | 0 | 40 | no
8.6 | 0 | 40 | no
8.7 | 0 | 40 | no
8.8 | 0 | 40 | no
8.9 | 0 | 40 | no
9 | 0 | 40 | no
9.1 | 0 | 40 | no
9.2 | 0 | 40 | no
9.3 | 0 | 40 | no
9.4 | 0 | 40 | no
9.5 | 0 | 40 | no
9.6 | 0 | 40 | no
9.7 | 0 | 40 | no
9.8 | 0 | 40 | no
9.9 | 0 | 40 | no
10 | 0 | 40 | no
10.1 | 0 | 40 | no
10.2 | 0 | 40 | no
10.3 | 0 | 40 | no
10.4 | 0 | 40 | no
10.5 | 0 | 40 | no
10.6 | 0 | 40 | no
10.7 | 0 | 40 | no
10.8 | 0 | 40 | no
10.9 | 0 | 40 | no
11 | 0 | 40 | no
11.1 | 0 | 40 | no
11.2 | 0 | 40 | no
11.3 | 0 | 40 | no
11.4 | 0 | 40 | no
11.5 | 0 | 40 | no
11.6 | 0 | 40 | no
11.7 | 0 | 40 | no
11.8 | 0 | 40 | no
11.9 | 0 | 40 | no
12 | 0 | 40 | no

## Parameters
Parameters
Blue on yellow = assumption you can change. Each value is a named cell (p_...).
Material and limits
Yield strength | 250 | MPa | Mild steel sheet
Elastic modulus | 200000 | MPa
Factor of safety on bending | 1.67 |  | Allowable stress = fy / factor
Splice efficiency on moment capacity | 0.55 |  | Coupler joint; applies to straight trays and channels, not to arms
Shear allowable, share of fy | 0.4 |  | Applied to the web area
Gravity | 9.81 | m/s²
Web depth / thickness limit | 200 |  | Flag only
Flange return / thickness limit | 60 |  | Flag only
Base plate width / thickness limit | 500 |  | Flag only
Cantilever tip deflection limit (arm length / x) | 100
Ladder tray
Side-rail return (collar) width | 25 | mm
Rung width | 50 | mm
Rung height | 20 | mm
Rung thickness | 2 | mm
Rungs per 2.5 m length | 10 | nos
Perforated tray (perforations in the base)
Holes per row | 4 | nos
Hole length | 10 | mm
Hole width | 20 | mm
Row spacing | 40 | mm
Trough tray
Holes per row | 2 | nos
Hole length | 10 | mm
Hole width | 20 | mm
Row spacing | 40 | mm
Channel and cantilever arm
Return lip width | 9 | mm
Beam coefficients (M = kw·w·L² + kp·P·L; V = kv·(w·L + P); d = dw·w·L⁴/EI + dp·P·L³/EI)
Support condition | kw | kp | dw | dp | kv
simple | 0.125 | 0.25 | 0.013021 | 0.020833 | 0.5
continuous | 0.1 | 0.2 | 0.0068966 | 0.009434 | 0.6
Ladder rung section (derived)
Rung base area | 100 | mm²
Rung side area (two legs) | 80 | mm²
Rung section area | 180 | mm²
Neutral axis from base | 5 | mm
Second moment of the rung | 6300 | mm⁴
Rung section modulus (smaller) | 420 | mm³